## Leak Volume Constants
Annex A | LEAK VOLUME CONSTANTS | [9 empty] | Annex B | LEAK VOLUME CONSTANTS
| Orifice / Leak Size (mm) | [10 empty] | Orifice / Leak Size (mm)
| 13mm (1/2 inch) |  | 25mm (3/4 inch) |  | 32mm (1 inch) |  | 50mm (1 1/2 inch) |  | 63mm (2 inch) |  |  | 75mm (3 inch) |  | 100mm (4 inch) |  | 125mm (5 inch) |  | 150mm (6 inch)
Pressure (PSI) | Volume in Cu.M./Min. |  | Volume in Cu.M./Min. |  | Volume in Cu.M./Min. |  | Volume in Cu.M./Min. |  | Volume in Cu.M./Min. |  | Pressure (PSI) | Volume in Cu.M./Min. |  | Volume in Cu.M./Min. |  | Volume in Cu.M./Min. |  | Volume in Cu.M./Min.
| PVC/PE | G.I. | PE | GI | PE | GI | PE | GI | PVC/PE | GI |  | PVC/PE | GI | PVC/ACP/PE | CI/GI | PVC/ACP/PE | CI/GI | PVC/ACP/PE | CI/GI
1 | 0.025497 | 0.022948 | 0.034928 | 0.031435 | 0.057226 | 0.051503 | 0.065529 | 0.058976 | 0.078815 | 0.070934 | 1 | 0.097879 | 0.088092 | 0.13237 | 0.11913 | 0.18796 | 0.16916 | 0.27193 | 0.24473
2 | 0.026772 | 0.024095 | 0.036674 | 0.033007 | 0.065809 | 0.059229 | 0.07418 | 0.066762 | 0.087574 | 0.078817 | 2 | 0.10679 | 0.096114 | 0.14156 | 0.12741 | 0.1976 | 0.17784 | 0.28225 | 0.25403
3 | 0.034421 | 0.030979 | 0.047152 | 0.042437 | 0.072963 | 0.065666 | 0.08139 | 0.073251 | 0.094874 | 0.085386 | 3 | 0.11422 | 0.1028 | 0.14923 | 0.1343 | 0.20564 | 0.18507 | 0.29086 | 0.26177
4 | 0.045895 | 0.041306 | 0.06287 | 0.056583 | 0.097284 | 0.087555 | 0.1059 | 0.095311 | 0.11969 | 0.10772 | 4 | 0.13948 | 0.12553 | 0.17528 | 0.15775 | 0.23297 | 0.20967 | 0.32012 | 0.28811
5 | 0.057369 | 0.051632 | 0.078587 | 0.070729 | 0.1216 | 0.10944 | 0.13041 | 0.11737 | 0.14451 | 0.13006 | 5 | 0.16473 | 0.14826 | 0.20133 | 0.18119 | 0.2603 | 0.23427 | 0.34938 | 0.31444
6 | 0.061193 | 0.055074 | 0.083827 | 0.075444 | 0.12876 | 0.11588 | 0.13762 | 0.12386 | 0.15181 | 0.13663 | 6 | 0.17216 | 0.15495 | 0.20899 | 0.18809 | 0.26833 | 0.2415 | 0.35799 | 0.32219
7 | 0.062468 | 0.056221 | 0.085573 | 0.077016 | 0.15022 | 0.1352 | 0.15925 | 0.14333 | 0.17371 | 0.15634 | 7 | 0.19445 | 0.175 | 0.23197 | 0.20877 | 0.29245 | 0.2632 | 0.3838 | 0.34542
8 | 0.071392 | 0.064253 | 0.097798 | 0.088018 | 0.17168 | 0.15451 | 0.18088 | 0.16279 | 0.1956 | 0.17604 | 8 | 0.21673 | 0.19506 | 0.25496 | 0.22946 | 0.31656 | 0.2849 | 0.40962 | 0.36866
9 | 0.080316 | 0.072285 | 0.11002 | 0.09902 | 0.19314 | 0.17382 | 0.20251 | 0.18226 | 0.2175 | 0.19575 | 9 | 0.23902 | 0.21511 | 0.27794 | 0.25015 | 0.34067 | 0.30661 | 0.43544 | 0.3919
10 | 0.08924 | 0.080316 | 0.12225 | 0.11002 | 0.2146 | 0.19314 | 0.22414 | 0.20172 | 0.2394 | 0.21546 | 10 | 0.2613 | 0.23517 | 0.30093 | 0.27083 | 0.36479 | 0.32831 | 0.46126 | 0.41513
11 | 0.098164 | 0.088348 | 0.13447 | 0.12102 | 0.22032 | 0.19829 | 0.2299 | 0.20691 | 0.24524 | 0.22071 | 11 | 0.26724 | 0.24052 | 0.30706 | 0.27635 | 0.37122 | 0.33409 | 0.46814 | 0.42133
12 | 0.10709 | 0.09638 | 0.1467 | 0.13203 | 0.24035 | 0.21631 | 0.25009 | 0.22508 | 0.26568 | 0.23911 | 12 | 0.28804 | 0.25924 | 0.32851 | 0.29566 | 0.39372 | 0.35435 | 0.49224 | 0.44301
13 | 0.11601 | 0.10441 | 0.15892 | 0.14303 | 0.26038 | 0.23434 | 0.27028 | 0.24325 | 0.28611 | 0.2575 | 13 | 0.30884 | 0.27796 | 0.34996 | 0.31496 | 0.41623 | 0.3746 | 0.51633 | 0.4647
14 | 0.12494 | 0.11244 | 0.17115 | 0.15403 | 0.28041 | 0.25237 | 0.29046 | 0.26142 | 0.30655 | 0.2759 | 14 | 0.32964 | 0.29668 | 0.37141 | 0.33427 | 0.43873 | 0.39486 | 0.54043 | 0.48639
15 | 0.13386 | 0.12047 | 0.18337 | 0.16503 | 0.30043 | 0.27039 | 0.31065 | 0.27958 | 0.32699 | 0.29429 | 15 | 0.35044 | 0.3154 | 0.39287 | 0.35358 | 0.46124 | 0.41511 | 0.56453 | 0.50807
16 | 0.14278 | 0.12851 | 0.1956 | 0.17604 | 0.32046 | 0.28842 | 0.33083 | 0.29775 | 0.34743 | 0.31269 | 16 | 0.37124 | 0.33412 | 0.41432 | 0.37289 | 0.48374 | 0.43537 | 0.58862 | 0.52976
17 | 0.15171 | 0.13654 | 0.20782 | 0.18704 | 0.34049 | 0.30644 | 0.35102 | 0.31592 | 0.36787 | 0.33108 | 17 | 0.39204 | 0.35284 | 0.43577 | 0.39219 | 0.50625 | 0.45562 | 0.61272 | 0.55145
18 | 0.16063 | 0.14457 | 0.22004 | 0.19804 | 0.36052 | 0.32447 | 0.37121 | 0.33409 | 0.3883 | 0.34947 | 18 | 0.41284 | 0.37155 | 0.45722 | 0.4115 | 0.52876 | 0.47588 | 0.63682 | 0.57314
19 | 0.16956 | 0.1526 | 0.23227 | 0.20904 | 0.38055 | 0.3425 | 0.39139 | 0.35225 | 0.40874 | 0.36787 | 19 | 0.43364 | 0.39027 | 0.47868 | 0.43081 | 0.55126 | 0.49613 | 0.66091 | 0.59482
20 | 0.17848 | 0.16063 | 0.24449 | 0.22004 | 0.40058 | 0.36052 | 0.41158 | 0.37042 | 0.42918 | 0.38626 | 20 | 0.45444 | 0.40899 | 0.50013 | 0.45012 | 0.57377 | 0.51639 | 0.68501 | 0.61651
21 | 0.1874 | 0.16866 | 0.25672 | 0.23105 | 0.42061 | 0.37855 | 0.43177 | 0.38859 | 0.44962 | 0.40466 | 21 | 0.47524 | 0.42771 | 0.52158 | 0.46942 | 0.59627 | 0.53664 | 0.70911 | 0.6382
22 | 0.19633 | 0.1767 | 0.26894 | 0.24205 | 0.44064 | 0.39657 | 0.45195 | 0.40676 | 0.47006 | 0.42305 | 22 | 0.49603 | 0.44643 | 0.54303 | 0.48873 | 0.61878 | 0.5569 | 0.7332 | 0.65988
23 | 0.20525 | 0.18473 | 0.28117 | 0.25305 | 0.46067 | 0.4146 | 0.47214 | 0.42492 | 0.49049 | 0.44145 | 23 | 0.51683 | 0.46515 | 0.56449 | 0.50804 | 0.64128 | 0.57716 | 0.7573 | 0.68157
24 | 0.21418 | 0.19276 | 0.29339 | 0.26405 | 0.4807 | 0.43263 | 0.49232 | 0.44309 | 0.51093 | 0.45984 | 24 | 0.53763 | 0.48387 | 0.58594 | 0.52735 | 0.66379 | 0.59741 | 0.7814 | 0.70326
25 | 0.2231 | 0.20079 | 0.30562 | 0.27506 | 0.50072 | 0.45065 | 0.51251 | 0.46126 | 0.53137 | 0.47823 | 25 | 0.55843 | 0.50259 | 0.60739 | 0.54665 | 0.68629 | 0.61767 | 0.80549 | 0.72494
26 | 0.23203 | 0.20882 | 0.31784 | 0.28606 | 0.52075 | 0.46868 | 0.5327 | 0.47943 | 0.55181 | 0.49663 | 26 | 0.57923 | 0.52131 | 0.62884 | 0.56596 | 0.7088 | 0.63792 | 0.82959 | 0.74663
27 | 0.24095 | 0.21685 | 0.33007 | 0.29706 | 0.54078 | 0.4867 | 0.55288 | 0.4976 | 0.57225 | 0.51502 | 27 | 0.60003 | 0.54003 | 0.6503 | 0.58527 | 0.73131 | 0.65818 | 0.85369 | 0.76832
28 | 0.24987 | 0.22489 | 0.34229 | 0.30806 | 0.56081 | 0.50473 | 0.57307 | 0.51576 | 0.59268 | 0.53342 | 28 | 0.62083 | 0.55875 | 0.67175 | 0.60457 | 0.75381 | 0.67843 | 0.87778 | 0.79
29 | 0.2588 | 0.23292 | 0.35452 | 0.31907 | 0.58084 | 0.52276 | 0.59326 | 0.53393 | 0.61312 | 0.55181 | 29 | 0.64163 | 0.57747 | 0.6932 | 0.62388 | 0.77632 | 0.69869 | 0.90188 | 0.81169
30 | 0.26772 | 0.24095 | 0.36674 | 0.33007 | 0.60087 | 0.54078 | 0.61344 | 0.5521 | 0.63356 | 0.5702 | 30 | 0.66243 | 0.59619 | 0.71465 | 0.64319 | 0.79882 | 0.71894 | 0.92597 | 0.83338
31 | 0.27665 | 0.24898 | 0.37897 | 0.34107 | 0.6209 | 0.55881 | 0.63363 | 0.57027 | 0.654 | 0.5886
32 | 0.28557 | 0.25701 | 0.39119 | 0.35207 | 0.64093 | 0.57683 | 0.65381 | 0.58843 | 0.67444 | 0.60699
33 | 0.29449 | 0.26504 | 0.40342 | 0.36307 | 0.66096 | 0.59486 | 0.674 | 0.6066 | 0.69487 | 0.62539
34 | 0.30342 | 0.27308 | 0.41564 | 0.37408 | 0.68099 | 0.61289 | 0.69419 | 0.62477 | 0.71531 | 0.64378
35 | 0.31234 | 0.28111 | 0.42786 | 0.38508 | 0.70101 | 0.63091 | 0.71437 | 0.64294 | 0.73575 | 0.66218
36 | 0.32127 | 0.28914 | 0.44009 | 0.39608 | 0.72104 | 0.64894 | 0.73456 | 0.6611 | 0.75619 | 0.68057
37 | 0.33019 | 0.29717 | 0.45231 | 0.40708 | 0.74107 | 0.66696 | 0.75475 | 0.67927 | 0.77663 | 0.69896
38 | 0.33911 | 0.3052 | 0.46454 | 0.41809 | 0.7611 | 0.68499 | 0.77493 | 0.69744 | 0.79706 | 0.71736
39 | 0.34804 | 0.31323 | 0.47676 | 0.42909 | 0.78113 | 0.70302 | 0.79512 | 0.71561 | 0.8175 | 0.73575
40 | 0.35696 | 0.32127 | 0.48899 | 0.44009 | 0.80116 | 0.72104 | 0.81531 | 0.73377 | 0.83794 | 0.75415
41 | 0.36589 | 0.3293 | 0.50121 | 0.45109 | 0.82119 | 0.73907 | 0.83549 | 0.75194 | 0.85838 | 0.77254
42 | 0.37481 | 0.33733 | 0.51344 | 0.46209 | 0.84122 | 0.7571 | 0.85568 | 0.77011 | 0.87882 | 0.79093
43 | 0.38373 | 0.34536 | 0.52566 | 0.4731 | 0.86125 | 0.77512 | 0.87586 | 0.78828 | 0.89925 | 0.80933
44 | 0.39266 | 0.35339 | 0.53789 | 0.4841 | 0.88127 | 0.79315 | 0.89605 | 0.80645 | 0.91969 | 0.82772
45 | 0.40158 | 0.36142 | 0.55011 | 0.4951 | 0.9013 | 0.81117 | 0.91624 | 0.82461 | 0.94013 | 0.84612
46 | 0.41051 | 0.36946 | 0.56234 | 0.5061 | 0.92133 | 0.8292 | 0.93642 | 0.84278 | 0.96057 | 0.86451
47 | 0.41943 | 0.37749 | 0.57456 | 0.51711 | 0.94136 | 0.84723 | 0.95661 | 0.86095 | 0.98101 | 0.88291
48 | 0.42835 | 0.38552 | 0.58679 | 0.52811 | 0.96139 | 0.86525 | 0.9768 | 0.87912 | 1.0014 | 0.9013
49 | 0.43728 | 0.39355 | 0.59901 | 0.53911 | 0.98142 | 0.88328 | 0.99698 | 0.89728 | 1.0219 | 0.91969
50 | 0.4462 | 0.40158 | 0.61124 | 0.55011 | 1.0014 | 0.9013 | 1.0172 | 0.91545 | 1.0423 | 0.93809

## Main
|  |  |  | 0.17604 |  |  | 0.12851 |  |  | 0.12851 |  |  | 0.17604 |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.17604 |  |  | 0.17604 |  |  | 0.12851 |  |  | 0.12851 |  |  | 0.17604 |  |  | 0.17604 |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.41432
DATE ACCOMPLISHED |  | ELEVATE/RELOCATE METER STAND |  |  | CHANGED METER |  |  | RECONNECTION |  |  | DRAIN | [5 empty] | FIRE USAGE |  |  | BUSTED | [8 empty] | LEAKS | [5 empty] | DISCONNECT FROM | [5 empty] | INSTALLATION OF APPURTENANCES |  |  | CONNECTION FROM MAIN LINE | [5 empty] | TOTAL
[11 empty] | METER STAND |  |  | MAINLINE | [5 empty] | MAIN LINE |  |  | SERVICE CONNECTION |  |  | METER STAND |  |  | CHANGE GATE/BALL VALVE |  |  | TAILPIECE |  |  | MAIN LINE |  |  | METER STAND | [5 empty] | LOOPING |  |  | INTERCONNECTION
|  | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m.
1 | 2022-09-01 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
2 | 2022-09-02 |  |  | 0 |  |  | 0 | 1 | 16 | 0 | 1 | 22 |  |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 25 | 4.4009 | 2 | 25 | 3.2127 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 5 | 88 | 7.6136
3 | 2022-09-03 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 6 | 0.77104 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 6 | 0.77104
4 | 2022-09-04 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
5 | 2022-09-05 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 10 | 1.7604 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 10 | 1.7604
6 | 2022-09-06 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 7 | 1.2323 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 7 | 1.2323
7 | 2022-09-07 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 15 | 1.9276 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 15 | 1.9276
8 | 2022-09-08 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
9 | 2022-09-09 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 20 | 2.5701 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 20 | 2.5701
10 | 2022-09-10 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
11 | 2022-09-11 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
12 | 2022-09-12 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
13 | 2022-09-13 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
14 | 2022-09-14 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 16 | 2.8166 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 16 | 2.8166
15 | 2022-09-15 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
16 | 2022-09-16 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 30 | 5.2811 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 30 | 5.2811
17 | 2022-09-17 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 | 1 | 10 | 1.7604 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 10 | 1.7604
18 | 2022-09-18 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
19 | 2022-09-19 |  |  | 0 |  |  |  | 1 | 5 | 0.64253 | 1 | 25 | 4.4009 |  |  | 0 |  |  | 0 | 1 | 60 | 24.8591 |  |  | 0 |  |  | 0 | 1 | 10 | 1.2851 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 4 | 100 | 31.1876
20 | 2022-09-20 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 10 | 1.2851 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 10 | 1.2851
21 | 2022-09-21 |  |  | 0 |  |  |  | 2 | 45 | 5.7828 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 35 | 6.1613 | 1 | 25 | 4.4009 | 1 | 16 | 2.0561 |  |  | 0 |  |  | 0 | 2 | 35 | 6.1613 |  |  | 0 |  |  | 0 |  |  | 0 | 7 | 156 | 24.5623
22 | 2022-09-22 |  |  | 0 |  |  |  | 1 | 19 | 2.4416 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 3 | 46 | 8.0977 |  |  | 0 |  |  | 0 |  |  | 0 | 4 | 65 | 10.5393
23 | 2022-09-23 |  |  | 0 | 1 | 15 |  |  |  | 0 | 2 | 50 | 8.8018 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 20 | 2.5701 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 3 | 70 | 11.3719
24 | 2022-09-24 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 25 | 4.4009 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 25 | 4.4009
25 | 2022-09-25 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
26 | 2022-09-26 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
27 | 2022-09-27 |  |  | 0 |  |  |  | 1 | 15 | 1.9276 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 20 | 3.5207 |  |  | 0 | 1 | 20 | 2.5701 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 3 | 55 | 8.0184
28 | 2022-09-28 |  |  | 0 | 1 | 15 |  | 1 | 12 | 1.5421 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 35 | 6.1613 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2 | 47 | 7.7033
29 | 2022-09-29 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
30 | 2022-09-30 | [21 empty] | 2 | 20
SUB-TOTAL |  | 0 | 0 | 0 | 2 | 30 | 0 | 7 | 112 | 12.3366 | 4 | 97 | 13.2027 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 60 | 24.8591 | 9 | 168 | 26.0533 | 2 | 50 | 8.8018 | 9 | 122 | 15.6778 | 1 | 20 | 2.5701 | 1 | 30 | 5.2811 | 6 | 91 | 16.0193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 730 | 124.8017
12.3366
22

## New Con Main
|  |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.17604 |  |  | 0.17604
DATE ACCOMPLISHED |  | NEW CONNECTION | [5 empty] | OPEN LINE | [5 empty] | TOTAL
|  | TAPPING/ TURN ON |  |  | ACROSS PAVEMENT |  |  | PLUG CONNECTION |  |  | RE-APPLICATION
|  | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m.
1 | 2022-08-23 |  |  | 0 |  |  | 0 | 1 | 30 | 5.2811 | 1 | 10 | 1.7604 | 2 | 40 | 7.0414
2 | 2022-08-24 |  |  | 0 |  |  | 0 | 1 | 35 | 6.1613 |  |  | 0 | 1 | 35 | 6.1613
3 | 2022-08-25 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
4 | 2022-08-26 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
5 | 2022-08-27 |  |  | 0 |  |  | 0 | 1 | 15 | 2.6405 | 1 | 20 | 3.5207 | 2 | 35 | 6.1613
6 | 2022-08-28 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
7 | 2022-08-29 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
8 | 2022-08-30 | 1 | 35 | 14.5012 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 35 | 14.5012
9 | 2022-08-31 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
10 | 2022-09-01 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
11 | 2022-09-02 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
12 | 2022-09-03 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
13 | 2022-09-04 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
14 | 2022-09-05 |  |  | 0 |  |  | 0 | 1 | 27 | 4.753 | 1 | 26 | 4.5769 | 2 | 53 | 9.3299
15 | 2022-09-06 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
16 | 2022-09-07 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
17 | 2022-09-08 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
18 | 2022-09-09 |  |  | 0 |  |  | 0 | 1 | 25 | 4.4009 |  |  | 0 | 1 | 25 | 4.4009
19 | 2022-09-10 | 1 | 1 | 0.41432 |  |  | 0 |  |  | 0 | 1 | 45 | 7.9216 | 2 | 46 | 8.3359
20 | 2022-09-11 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
21 | 2022-09-12 |  |  | 0 | 1 | 225 | 93.2217 |  |  | 0 |  |  | 0 | 1 | 225 | 93.2217
22 | 2022-09-13 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
23 | 2022-09-14 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
24 | 2022-09-15 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 9 | 1.5843 | 1 | 9 | 1.5843
25 | 2022-09-16 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
26 | 2022-09-17 | 1 | 20 | 8.2864 |  |  | 0 | 1 | 15 | 2.6405 |  |  | 0 | 2 | 35 | 10.9269
27 | 2022-09-18 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
28 | 2022-09-19 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
29 | 2022-09-20 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 5 | 0.88018 | 1 | 5 | 0.88018
30 | 2022-09-21 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
30 | 2022-09-22 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
SUB-TOTAL |  | 3 | 56 | 23.2018 | 1 | 225 | 93.2217 | 6 | 147 | 25.8773 | 6 | 115 | 20.2441 | 16 | 543 | 162.5449
[7 empty] | 116.4235 | [5 empty] | 46.1214
1899-12-31

## Sub
|  |  |  | 0.17604 |  |  | 0.12851 |  |  | 0.12851 |  |  | 0.17604 |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.17604 |  |  | 0.17604 |  |  | 0.12851 |  |  | 0.12851 |  |  | 0.17604 |  |  | 0.17604 |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.41432
DATE ACCOMPLISHED |  | ELEVATE/RELOCATE METER STAND |  |  | CHANGED METER |  |  | RECONNECTION |  |  | DRAIN | [5 empty] | FIRE USAGE |  |  | BUSTED | [8 empty] | LEAKS | [5 empty] | DISCONNECT FROM | [5 empty] | INSTALLATION OF APPURTENANCES |  |  | CONNECTION FROM MAIN LINE | [5 empty] | TOTAL
[11 empty] | METER STAND |  |  | MAINLINE | [5 empty] | MAIN LINE |  |  | SERVICE CONNECTION |  |  | METER STAND |  |  | CHANGE GATE /BALL VALVE |  |  | TAILPIECE |  |  | MAIN LINE |  |  | METER STAND | [5 empty] | LOOPING |  |  | INTERCONNECTION
|  | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m.
1 | 2022-09-01 |  |  | 0 | [5 empty] | 0 | 1 | 26 | 4.5769 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 26 | 4.5769
2 | 2022-09-02 |  |  | 0 | 6 | 83 | 10.666 |  |  | 0 | 2 | 34 | 5.9852 | 2 | 24 | 9.9436 |  |  | 0 |  |  | 0 | 2 | 170 | 29.9261 |  |  | 0 | 1 | 10 | 1.2851 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 13 | 321 | 57.806
3 | 2022-09-03 |  |  | 0 | 6 | 44 | 5.6543 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 29 | 5.105 |  |  | 0 | 1 | 10 | 1.2851 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 8 | 83 | 12.0444
4 | 2022-09-04 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
5 | 2022-09-05 |  |  | 0 | 11 | 99 | 12.7221 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 125 | 22.0045 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 12 | 224 | 34.7266
6 | 2022-09-06 |  |  | 0 | 9 | 60 | 7.7104 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 3 | 21 | 2.6986 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 12 | 81 | 10.409
7 | 2022-09-07 |  |  | 0 | 37 | 592 | 76.0757 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2 | 20 | 2.5701 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 39 | 612 | 78.6458
8 | 2022-09-08 |  |  | 0 | 13 | 78 | 10.0235 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 2 | 20 | 2.5701 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 15 | 98 | 12.5936
9 | 2022-09-09 |  |  | 0 | 15 | 133 | 17.0913 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 30 | 5.2811 |  |  |  | 1 | 14 | 1.7991 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 17 | 177 | 24.1715
10 | 2022-09-10 |  |  | 0 | 1 | 16 | 2.0561 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 16 | 2.0561
11 | 2022-09-11 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
12 | 2022-09-12 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
13 | 2022-09-13 |  |  | 0 | 15 | 75 | 9.638 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 15 |  | 9.638
14 | 2022-09-14 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  |  | 2 | 20 | 2.5701 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2 | 20 | 2.5701
15 | 2022-09-15 |  |  | 0 | 11 | 55 | 7.0678 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | #VALUE! | 55 | 7.0678
16 | 2022-09-16 |  |  | 0 | 15 | 79 | 10.152 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 199 | 35.0311 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 16 | 278 | 45.1831
17 | 2022-09-17 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
18 | 2022-09-18 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 80 | 14.0829 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 80 | 14.0829
19 | 2022-09-19 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 60 | 10.5622 | [5 empty] | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 60 | 10.5622
20 | 2022-09-20 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | 0 | 1 | 210 | 87.0069 | 1 | 15 | 2.6405 |  |  | 0 | 1 | 15 | 1.9276 | 1 | 20 | 2.5701 |  |  | 0 | 1 | 10 | 1.7604 |  |  | 0 |  |  | 0 |  |  | 0 | 5 | 270 | 95.9055
21 | 2022-09-21 |  |  | 0 | 1 | 20 | 2.5701 | 1 | 15 | 1.9276 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2 | 40 | 7.0414 |  |  | 0 |  |  | 0 |  |  | 0 | 4 | 75 | 11.5392
22 | 2022-09-22 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 5 | 15 | 2.6405 |  |  | 0 |  |  | 0 |  |  | 0 | 5 | 15 | 2.6405
23 | 2022-09-23 | 15 | 162 | 28.5178 |  |  | 0 | 1 | 10 | 1.2851 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 7 | 70 | 8.9954 |  |  | 0 |  |  | 0 | 2 | 31 | 5.4571 |  |  | 0 |  |  | 0 |  |  | 0 | 10 | 111 | 15.7376
24 | 2022-09-24 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 75 | 31.0739 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 75 | 31.0739
25 | 2022-09-25 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 3 | 430 | 75.6954 |  |  | 0 | 2 | 30 | 3.8552 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 5 | 460 | 79.5506
26 | 2022-09-26 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 2 | 322 | 56.6836 |  |  | 0 | 1 | 20 | 2.5701 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 3 | 342 | 59.2537
27 | 2022-09-27 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 45 | 7.9216 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 |  | 7.9216
28 | 2022-09-28 |  |  | 0 | 1 | 30 | 3.8552 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 30 | 5.2811 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 150 | 62.1478 |  |  | 0 |  |  | 0 | 3 | 210 | 71.2841
29 | 2022-09-29 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 125 | 51.7898 | 3 | 94 | 16.5474 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 4 | 219 | 68.3372
30 | 2022-09-30 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
30 | 2022-10-01 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 55 | 22.7875 |  |  | 0 | 1 | 45 | 7.9216 | 1 | 18 | 2.3131 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 3 | 118 | 33.0222
SUB-TOTAL |  | 15 | 162 | 28.5178 | 141 | 1364 | 175.2824 | 2 | 25 | 3.2127 | 3 | 60 | 10.5622 | 2 | 24 | 9.9436 | 0 | 0 | 0 | 3 | 410 | 169.8706 | 19 | 1629 | 286.7625 | 0 | 0 | 0 | 23 | 250 | 32.1265 | 1 | 20 | 2.5701 | 0 | 0 | 0 | 10 | 96 | 16.8994 | 1 | 150 | 62.1478 | 0 | 0 | 0 | 0 | 0 | 0 | #VALUE! | 3908 | 769.3779
207.0129
46

## New Con Sub
|  |  |  | 0.41432 |  |  | 0.41432 |  |  | 0.17604 |  |  | 0.17604
DATE |  | NEW CONNECTION | [5 empty] | OPEN LINE | [5 empty] | TOTAL
|  | TAPPING/ TURN ON |  |  | ACROSS PAVEMENT |  |  | PLUG CONNECTION |  |  | RE-APPLICATION
|  | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m. | # of JO | Minutes | cu.m.
1 | 2022-08-23 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
2 | 2022-08-24 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
3 | 2022-08-25 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
4 | 2022-08-26 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
5 | 2022-08-27 | 1 | 14 | 5.8005 |  |  | 0 |  |  | 0 |  |  | 0 | 1 | 14 | 5.8005
6 | 2022-08-28 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
7 | 2022-08-29 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
8 | 2022-08-30 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
9 | 2022-08-31 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
10 | 2022-09-01 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
11 | 2022-09-02 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
12 | 2022-09-03 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
13 | 2022-09-04 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
14 | 2022-09-05 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
15 | 2022-09-06 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
16 | 2022-09-07 |  |  | 0 | 1 | 24 | 9.9436 |  |  | 0 |  |  | 0 | 1 | 24 | 9.9436
17 | 2022-09-08 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
18 | 2022-09-09 |  |  | 0 | 1 | 60 | 24.8591 | 1 | 15 | 2.6405 |  |  | 0 | 2 | 75 | 27.4997
19 | 2022-09-10 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
20 | 2022-09-11 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
21 | 2022-09-12 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
22 | 2022-09-13 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
23 | 2022-09-14 |  |  | 0 |  |  | 0 | 1 | 10 | 1.7604 |  |  | 0 | 1 | 10 | 1.7604
24 | 2022-09-15 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
25 | 2022-09-16 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
26 | 2022-09-17 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
27 | 2022-09-18 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
28 | 2022-09-19 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
29 | 2022-09-20 |  |  | 0 |  |  | 0 | 1 | 40 | 7.0414 | 1 | 8 | 1.4083 | 2 | 48 | 8.4497
30 | 2022-09-21 |  |  | 0 |  |  | 0 |  |  | 0 |  |  | 0 | 0 | 0 | 0
31 | 08/22/22
SUB-TOTAL |  | 1 | 14 | 5.8005 | 2 | 84 | 34.8028 | 3 | 65 | 11.4423 | 1 | 8 | 1.4083 | 7 | 171 | 53.4538
[7 empty] | 40.6032 | [5 empty] | 12.8506