## MNF Graph -dma3
Minimum Night Flow
August 11, 2020
DMA4
TIME | DEL PILAR FM #1- inflow | Cu. M.
12:00 MN | 6565
1:00 | 6570 | 5
2:00 | 6576 | 6
3:00 | 6581 | 5
4:00 | 6588 | 7

## Analysis
ANALYSIS OF COMPONENTS OF NRW
DMA 4
| JULY 2020 NRW Volume |  |  | 12112
| Minimum Night Flow |  | 5 CU.M | 3720
| NRW COMPONENTS |  | CUBIC METER | % TO TOTAL
| Total NRW Volume |  | 12112 | 100%
|  | Physical | 3720 | 30.71%
|  | Commercial | 8392 | 69.29%

## DMA FM
DMA FLOW METER READING
As of JULY 2020
| STA. CRUZ FM #1- Inflow |  |  | STA. CRUZ FM #2- outflow |  |  | DEL PILAR FM #1- inflow |  |  | DEL PILAR FM #2- outflow |  |  | SAN VICENTE FM #1- bypass |  |  | SAN VICENTE FM #2- outflow
DATE | START | OFF | CU. M. | START | OFF | CU. M. | START | OFF | CU. M. | START | OFF | CU. M. | START | OFF | CU. M. | START | OFF | CU. M.
2020-06-30 | 128390 | 128424 | 34 | 342113 | 342270 | 157 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 103414 | 103414 | 80 | 259782 | 260004 | 222
2020-07-01 | 128424 | 128488 | 64 | 342270 | 342406 | 136 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 103414 | 103505 | 91 | 260004 | 260205 | 201
2020-07-02 | 128488 | 128568 | 80 | 342406 | 342566 | 160 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 103505 | 103583 | 78 | 260205 | 260442 | 237
2020-07-03 | 128568 | 128628 | 60 | 342566 | 342728 | 162 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 103583 | 103671 | 88 | 260442 | 260682 | 240
2020-07-04 | 128628 | 128678 | 50 | 342728 | 342902 | 174 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 103671 | 103738 | 67 | 260682 | 260922 | 240
2020-07-05 | 128678 | 128730 | 52 | 342902 | 343059 | 157 | ave due to stuck-up |  | 79 | 209902 | 209917 | 15 | 103738 | 103818 | 80 | 260922 | 261176 | 254
2020-07-06 | 128730 | 128796 | 66 | 343059 | 343181 | 122 | 5817 | 5854 | 37 | 209917 | 209933 | 16 | 103818 | 103885 | 67 | 261176 | 261480 | 304
2020-07-07 | 128796 | 128855 | 59 | 343181 | 343312 | 131 | 5854 | 5902 | 48 | 209933 | 209933 | 0 | 103885 | 103965 | 80 | 261480 | 261734 | 254
2020-07-08 | 128855 | 128924 | 69 | 343312 | 343567 | 255 | 5902 | 5983 | 81 | 209933 | 209939 | 6 | 103965 | 104043 | 78 | 261734 | 261970 | 236
2020-07-09 | 128924 | 128989 | 65 | 343567 | 343640 | 73 | 5983 | 6071 | 88 | 209939 | 209950 | 11 | 104043 | 104116 | 73 | 261970 | 262228 | 258
2020-07-10 | 128989 | 129072 | 83 | 343640 | 343713 | 73 | 6071 | 6183 | 112 | 209950 | 209954 | 4 | 104116 | 104202 | 86 | 262228 | 262469 | 241
2020-07-11 | 129072 | 129134 | 62 | 343713 | 343843 | 130 | 6183 | 6295 | 112 | 209954 | 209964 | 10 | 104202 | 104286 | 84 | 262469 | 262717 | 248
2020-07-12 | 129134 | 129220 | 86 | 343843 | 343983 | 140 | ave due to stuck-up |  | 79 | 209964 | 209976 | 12 | 104286 | 104363 | 77 | 262717 | 262976 | 259
2020-07-13 | 129220 | 129275 | 55 | 343983 | 344110 | 127 | ave due to stuck-up |  | 79 | 209976 | 209996 | 20 | 104363 | 104432 | 69 | 262976 | 263201 | 225
2020-07-14 | 129275 | 129343 | 68 | 344110 | 344239 | 129 | ave due to stuck-up |  | 79 | 209996 | 210009 | 13 | 104432 | 104515 | 83 | 263201 | 263433 | 232
2020-07-15 | 129343 | 129410 | 67 | 344239 | 344382 | 143 | ave due to stuck-up |  | 79 | 210009 | 210022 | 13 | 104515 | 104591 | 76 | 263433 | 263722 | 289
2020-07-16 | 129410 | 129488 | 78 | 344382 | 344518 | 136 | ave due to stuck-up |  | 79 | 210022 | 210022 | 0 | 104591 | 104604 | 13 | 263722 | 264004 | 282
2020-07-17 | 129488 | 129546 | 58 | 344518 | 344670 | 152 | ave due to stuck-up |  | 79 | 210022 | 210122 | 100 | 104604 | 104679 | 75 | 264004 | 264306 | 302
2020-07-18 | 129546 | 129602 | 56 | 344670 | 344839 | 169 | ave due to stuck-up |  | 79 | 210122 | 210138 | 16 | 104679 | 104747 | 68 | 264306 | 264603 | 297
2020-07-19 | 129602 | 129708 | 106 | 344839 | 345021 | 182 | ave due to stuck-up |  | 79 | 210138 | 210156 | 18 | 104747 | 104818 | 71 | 264603 | 264885 | 282
2020-07-20 | 129708 | 129712 | 4 | 345021 | 345199 | 178 | ave due to stuck-up |  | 79 | 210156 | 210168 | 12 | 104818 | 104880 | 62 | 264885 | 265138 | 253
2020-07-21 | 129712 | 129900 | 188 | 345199 | 345339 | 140 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 104880 | 104965 | 85 | 265138 | 265418 | 280
2020-07-22 | 129900 | 129959 | 59 | 345339 | 345502 | 163 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 104965 | 105028 | 63 | 265418 | 265652 | 234
2020-07-23 | 129959 | 130070 | 111 | 345502 | 345645 | 143 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105028 | 105115 | 87 | 265652 | 265917 | 265
2020-07-24 | 130070 | 130129 | 59 | 345645 | 345784 | 139 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105115 | 105231 | 116 | 265917 | 266121 | 204
2020-07-25 | 130129 | 130186 | 57 | 345784 | 345934 | 150 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105231 | 105336 | 105 | 266121 | 266345 | 224
2020-07-26 | 130186 | 130247 | 61 | 345934 | 346078 | 144 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105336 | 105442 | 106 | 266345 | 266605 | 260
2020-07-27 | 130247 | 130313 | 66 | 346078 | 346268 | 190 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105442 | 105532 | 90 | 266605 | 266860 | 255
2020-07-28 | 130313 | 130435 | 122 | 346268 | 346439 | 171 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105532 | 105628 | 96 | 266860 | 267098 | 238
2020-07-29 | 130435 | 130528 | 93 | 346439 | 346582 | 143 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105628 | 105727 | 99 | 267098 | 267336 | 238
2020-07-30 | 130528 | 130650 | 122 | 346582 | 346734 | 152 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105727 | 105821 | 94 | 267336 | 267547 | 211
2020-07-31 | 130650 | 130727 | 77 | 346734 | 346797 | 63 | ave due to stuck-up |  | 79 | ave due to stuck-up |  | 16 | 105821 | 105899 | 78 | 267547 | 267813 | 266
TOTAL PROD. |  |  | 2337 |  |  | 4684 |  |  | 2532 |  |  | 522 |  |  | 2565 |  |  | 8031
Formulas:
DATE = [DATE, row above]+1
Note on A6: Joy Cenizal: base on cut-off 5pm onwards

## DMA Con
DMA 1 |  |  |  |  | DMA 2 |  |  |  |  | DMA 4 |  |  |  |  | DMA 3
Book | Res | Com | Total | Cust Billed | Book | Res | Com | Total | Cust Billed | Book | Res | Com | Total | Cust Billed | Book | Res | Com | Total | Cust Billed
310 | 406 | 17 | 423 | 23 | 140 | 7926 | 735 | 8661 | 374 | 130 | 5312 | 10 | 5322 | 230 | 110 | 7766 | 10 | 7776 | 408
320 | 3875 | 5 | 3880 | 176 | 210 | 7925 | 157 | 8082 | 368 | 150 | 4738 | 82 | 4820 | 244 | 120 | 6128 | 12 | 6140 | 272
330 | 4598 | 234 | 4832 | 239 | 220 | 6798 | 31 | 6829 | 304 | 170 | 3449 | 9 | 3458 | 177 | 160 | 3630 | 120 | 3750 | 179
340 | 2787 | 9 | 2796 | 150 | 230 | 7226 | 1668 | 8894 | 399 | 190 | 5001 | 13 | 5014 | 257 | 420 | 5139 | 0 | 5139 | 280
410 | 4562 | 0 | 4562 | 232 | 240 | 10548 | 450 | 10998 | 504 |  | 18500 | 114 | 18614 | 908 | 430 | 2546 | 214 | 2760 | 135
440 | 2574 | 0 | 2574 | 135 | 310 | 4531 | 41 | 4572 | 209 | [6 empty] | 25209 | 356 | 25565 | 1274
| 18802 | 265 | 19067 | 955 | 350 | 2053 | 0 | 2053 | 114
[5 empty] | 360 | 10445 | 225 | 10670 | 539
[6 empty] | 57452 | 3307 | 60759 | 2811
| Res | Com | Total | Billed Cust.
DMA 1 | 18802 | 265 | 19067 | 955
DMA 2 | 57452 | 3307 | 60759 | 2811
DMA 3 | 25209 | 356 | 25565 | 1274
DMA 4 | 18500 | 114 | 18614 | 908
| 119963 | 4042 | 124005 | 5948

## NRW Per DMA
NRW PER DMA | [17 empty] | PRODUCTION CAPACITY ANALYSIS
[18 empty] | DAILY DEMAND |  |  |  | INSTALLED PRODUCTION CAPACITY |  |  |  | REMARKS
DMA | No. of Billed Cust. | Billed Cons |  |  |  | No. Of Billing Days | Ave Cons. |  |  | Inflow |  | Outflow |  | Supply | NRW |  | REMARKS | Cons/Day | ADD | MDD |  | PUMPS | BULK PURCHASE | TOTAL | % Vs. MDD
|  | Residential | Commercial | Bulk | Total |  | Per Cust/Mo | Per HH/Mo | Per Capita/Day | Location / Source | Volume | Location / Source | Volume |  | Volume | %
|  | Cu M | Cu M | Cu M | Cu M |  | Cu M | Cu M | Liters |  | Cu M |  | Cu M | Cu M | Cu M |  |  | Cu M | Cu M | Cu M | GPM | GPM | GPM | GPM
1 | 932 | 18396 | 248 |  | 18644 | 31 | 20.0043 | 20.0043 | 129.0599 | PUMP #2 | 21213.8294 | Sta. Cruz FM#2 | 4684 | 18866.8294 | 222.8294 | 1.181% |  | 583.9355 | 595.8065 | 774.5484 | 141.8587 |  | 0 | 0 | 0
[10 empty] | Sta. Cruz FM#1 | 2337 |  |  | #REF!
#REF!
2 | 3106 | 63986 | 3336 |  | 67322 | 31 | 21.6748 | 21.6748 | 139.8376 | PUMP #1 | 52312.4283 | San Vicente FM#1 bypass | 2565 | 70663.4586 | 3341.4586 | 4.729% |  | 1926.871 | 2126.3226 | 2764.2194 | 506.2673 |  | 0 | 0 | 0
[10 empty] | PUMP #5 | 13070.0303 | Del Pilar FM#1 | 2532
[10 empty] | Sta. Cruz FM#2 | 4684 | Sta. Cruz FM#1 | 2337 | #REF!
[10 empty] | San Vicente FM#2 | 8031
#REF!
3 | 1087 | 22130 | 234 |  | 22364 | 31 | 20.5741 | 20.5741 | 132.7359 | PUMP #4 | 28030.455 | San Vicente FM#2 | 8031 | 23086.455 | 722.455 | 3.129% |  | 737.1935 | 922.6452 | 1199.4387 | 219.6774 |  | 0 | 0 | 0
[10 empty] | San Vicente FM#1 bypass | 2565 |  |  | #REF!
[10 empty] | Del Pilar FM#2 | 522 |  |  | #REF!
4 | 823 | 15451 | 224 |  | 15675 | 31 | 19.0462 | 19.0462 | 122.8785 | PUMP #3 | 25777.4256 | Del Pilar FM#2 | 522 | 27787.4256 | 12112.4256 | 43.59% |  | 353.9032 | 374.2258 | 486.4935 | 89.1014 |  | 0 | 0 | 0
[10 empty] | Del Pilar FM#1 | 2532
5 |  |  |  |  | 0 |  | #DIV/0! | #DIV/0! | #DIV/0! |  |  |  |  | 0 | 0 | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  |  | 0 | #DIV/0!
Total | 5948 | 119963 | 4042 | 0 | 124005 | 31 | 20.8482 | 20.8482 | 134.5044 |  | 161075.1685 |  | 15987 | 140404.1685 | 16399.1685 | 11.68% |  | 3601.9032 | 4019 | 5224.7 | 956.9048 | 0 | 0 | 0 | 0

## LVC
BOOK | AREAS | PSI | 1/2 inch | 3/4 inch |  | 1" |  | 2" | 3" | 4" | 6"
|  |  | G.I Pipe | P.E | G.I | P.E | G.I | PVC | PVC | PVC | PVC
110 | Sto. Rosario- old | 16 | 0.12851 | 0.1956 | 0.17604 |  |  | 0.34743 | 0.37124 | 0.41432 | 0.58862
120 | Sto. Rosario- young | 15 | 0.12047 | 0.18337 | 0.16503 |  |  | 0.32699 | 0.35044 | 0.39287 | 0.56453
130 | Del Pilar- west | 13 | 0.10441 | 0.15892 | 0.14303 |  |  | 0.28611 | 0.30884 | 0.34996 | 0.51633
140 | Del Pilar- east | 12 | 0.09638 | 0.1467 | 0.13203 |  |  | 0.26568 | 0.28804 | 0.32851 | 0.49224
150 | San Vicente | 16 | 0.12851 | 0.1956 | 0.17604 |  |  | 0.34743 | 0.37124 | 0.41432 | 0.58862
160 | Sto. Rosario- Phase 2 | 13 | 0.10441 | 0.15892 | 0.14303 |  |  | 0.28611 | 0.30884 | 0.34996 | 0.51633
170 | San Rafael | 14 | 0.11244 | 0.17115 | 0.15403 |  |  | 0.30655 | 0.32964 | 0.37141 | 0.54043
190 | Sta.Lucia- young | 8 | 0.06425 | 0.0978 | 0.08802 |  |  | 0.1956 | 0.21673 | 0.25496 | 0.40962
210 | Concepcion- west | 16 | 0.12851 | 0.1956 | 0.17604 |  |  | 0.34743 | 0.37124 | 0.41432 | 0.58862
220 | concepcion- east | 20 | 0.16063 | 0.24449 | 0.22004 |  |  | 0.42918 | 0.45444 | 0.50013 | 0.68501
230 | San Isidro-1 | 18 | 0.14457 | 0.22004 | 0.19804 |  |  | 0.3883 | 0.41284 | 0.45722 | 0.63682
240 | San Isidro-2 | 22 | 0.1767 | 0.26894 | 0.24205 |  |  | 0.47006 | 0.49603 | 0.54303 | 0.7332
310 | Sta. Cruz | 25 | 0.20079 | 0.30562 | 0.27506 |  |  | 0.53137 | 0.55843 | 0.60739 | 0.80549
320 | Pantoc | 20 | 0.16063 | 0.24449 | 0.22004 |  |  | 0.42918 | 0.45444 | 0.50013 | 0.68501
330 | Carmen-1 | 20 | 0.16063 | 0.24449 | 0.22004 |  |  | 0.42918 | 0.45444 | 0.50013 | 0.68501
340 | Carmen-2 | 18 | 0.14457 | 0.22004 | 0.19804 |  |  | 0.3883 | 0.41284 | 0.45722 | 0.63682
350 | Manaul | 30 | 0.20079 | 0.30562 | 0.27506 |  |  | 0.63356 | 0.55843 | 0.60739 | 0.80549
360 | Batitang | 35 | 0.20079 | 0.30562 | 0.27506 |  |  | 0.73575 | 0.55843 | 0.60739 | 0.80549
410 | Gen. Luna | 25 | 0.20079 | 0.30562 | 0.27506 |  |  | 0.73575 | 0.55843 | 0.60739 | 0.80549
420 | Macarse | 10 | 0.08032 | 0.12225 | 0.11002 |  |  | 0.2394 | 0.2613 | 0.30093 | 0.46126
430 | Mayamot | 8 | 0.06425 | 0.0978 | 0.08802 |  |  | 0.1956 | 0.21673 | 0.25496 | 0.40962
440 | H. Romero | 22 | 0.1767 | 0.26894 | 0.24205 |  |  | 0.47006 | 0.49603 | 0.54303 | 0.7332

## COMPUTATION (2)
BWSI- ZARAGOZA BRANCH
W.B. INPUT DATA COMPUTATION
JUNE 30 to JULY 29 2020 |  |  |  |  | 31 days
DATE | J.O # |  | SL AND ML |  | DURATION | CU.M/MIN. | SERVICE CONNECTION DRAINING |  |  |  | DRAINING |  | Disconnection |  | ACCOUNTED LEAKAGES
|  | PARTICULARS | SIZE | ADDRESS | IN MINS. |  | TAP/ AS | PLUG/OL/REC | A. PAVEMENT | RELOCATION | MAINLINE | M-STAND | M. Stand | Mainline | SVC PIPE | MAINLINE | METERSTAND | T-PIECE | GATEVALVE
2020-06-30 10:57 | JO12-0620-0214 | METERING CONCERNS (BUSTED METER STAND) | 0.75 | DEL PILAR (E), DEL PILAR, ZARAGOZA, NU... | 102 | [11 empty] | 14.9634
2020-06-30 15:46 | JO12-0620-0225 | METERING CONCERNS (TAIL PIECE LEAKING) | 0.5 | , MACARSE, ZARAGOZA, NUEVA ECIJA | 4 | [12 empty] | 0.32128
2020-07-01 11:50 | JO12-0620-0205 | REPAIRS AND MAINTENANCE (BUSTED PIPE) | 0.75 | WEST, DEL PILAR, ZARAGOZA, NUEVA ECIJA | 20 | [9 empty] | 2.8606
2020-07-01 11:05 | JO12-0720-0002 | METERING CONCERNS (BUSTED PIPE) | 0.75 | SITIO PUTOT, BATITANG, ZARAGOZA, NUEVA... | 20 | [9 empty] | 6.1124
2020-07-01 14:30 | JO12-0720-0006 | REPAIRS AND MAINTENANCE (BUSTED PIPE) | 0.75 | WEST, DEL PILAR, ZARAGOZA, NUEVA ECIJA | 60 | [9 empty] | 9.5352
2020-07-03 14:15 | JO12-0620-0220 | METERING CONCERNS (BROKEN TAIL PIECE) | 0.5 | , GENERAL LUNA, ZARAGOZA, NUEVA ECIJA | 5 | [12 empty] | 1.0039
2020-07-03 15:00 | JO12-0620-0221 | METERING CONCERNS (BROKEN TAIL PIECE) | 0.5 | STA. CRUZ, STA. CRUZ, ZARAGOZA, NUEVA... | 15 | [12 empty] | 3.0118
2020-07-03 11:30 | JO12-0620-0227 | METERING CONCERNS (BUSTED PIPE) | 0.75 | , SAN VICENTE (POBLACION), ZARAGOZA, N... | 150 | [9 empty] | 26.406
2020-07-03 11:30 | JO12-0620-0228 | METERING CONCERNS (BUSTED PIPE) | 0.75 | , SAN VICENTE (POBLACION), ZARAGOZA, N... | 150 | [9 empty] | 26.406
2020-07-03 11:30 | JO12-0620-0229 | METERING CONCERNS (BUSTED PIPE) | 0.75 | , SAN VICENTE (POBLACION), ZARAGOZA, N... | 150 | [9 empty] | 26.406
2020-07-03 15:25 | JO12-0720-0069 | METERING CONCERNS (BUSTED PIPE) | 0.75 | , STA. CRUZ, ZARAGOZA, NUEVA ECIJA | 10 | [9 empty] | 2.7506
2020-07-06 10:30 | JO12-0720-0078 | METERING CONCERNS (BUSTED PIPE) | 0.75 | CONCEPCION (E), CONCEPCION, ZARAGOZA,... | 110 | [9 empty] | 24.2044
2020-07-06 12:00 | JO12-0720-0079 | METERING CONCERNS (BUSTED PIPE) | 0.75 | PUROK LAKATAN, CONCEPCION (W), CONCEPC... | 80 | [9 empty] | 14.0832
2020-07-06 16:30 | JO12-0720-0081 | METERING CONCERNS (BUSTED PIPE) | 0.75 | PUROK 7,PAHSE 1 SAN ISIDRO, ZARAGOZA, NUEVA E... | 180 | [9 empty] | 35.6472
2020-07-08 09:50 | JO12-0620-0182 | NEW CONNECTION/ PLUG CONNECTION | P | PHASE 2 PUROK 1, CTM, SAN ISIDRO, ZARAGOZA, NU... | 3 |  |  | 0.43371
2020-07-08 09:15 | JO12-0620-0196 | NEW CONNECTION/ PLUG CONNECTION | P | PUROK 2, TBA, GENERAL LUNA, ZARAGOZA,... | 3 |  |  | 0.60237
2020-07-08 11:29 | JO12-0720-0083 | NEW CONNECTION/ OPEN MAINLINE | O | PUROK 1, CDD, STO. ROSARIO OLD, ZARAGO... | 3 |  |  | 0.38553
2020-07-08 16:05 | JO12-0720-0077 | NEW CONNECTION/ TAPPING |  | ROSEMAR VILLAGE, MPD, PHASE 2,CARMEN, ZARAGOZA... | 3 |  | 0.43371
2020-07-08 14:15 | JO12-0620-0177 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, EMG,PHASE 1 STO. ROSARIO YOUNG, ZARA... | 3 |  |  | 0.36141
2020-07-08 14:40 | JO12-0620-0195 | NEW CONNECTION/ OPEN MAINLINE |  | EAST, VCG, DEL PILAR, ZARAGOZA, NUEVA... | 3 |  |  | 0.28914
2020-07-08 18:30 | JO12-0720-0101 | METERING CONCERNS (BUSTED METER STAND) | 0.75 | , STO. ROSARIO YOUNG, ZARAGOZA, NUEVA... | 30 | [11 empty] | 4.9509
2020-07-09 10:15 | JO12-0620-0137 | NEW CONNECTION/ PLUG CONNECTION |  | WEST, VDP, CONCEPCION, ZARAGOZA, NUEVA... | 3 |  |  | 0.38553
2020-07-09 09:40 | JO12-0720-0059 | NEW CONNECTION/ TAPPING |  | -(A)/ PUROK 1, STO. ROSARIO OLD, STO.... | 3 |  | 0.38553
2020-07-09 10:38 | JO12-0720-0090 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, RSD, PANTOC, ZARAGOZA, NUEVA... | 3 |  |  | 0.48189
2020-07-09 11:28 | JO12-0720-0100 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 6, ADC, GENERAL LUNA, ZARAGOZA,... | 3 |  |  | 0.60237
2020-07-09 10:02 | JO12-0720-0096 | NEW CONNECTION/ TAPPING |  | PUROK 5, KSB, SAN RAFAEL, ZARAGOZA, NU... | 3 |  | 0.33732
2020-07-09 10:20 | JO12-0720-0097 | NEW CONNECTION/ PLUG CONNECTION |  | -(B)/ PUROK 5, KSB, SAN RAFAEL, ZARAGO... | 3 |  |  | 0.33732
2020-07-09 11:05 | JO12-0720-0098 | NEW CONNECTION/ PLUG CONNECTION |  | -(A)/ PUROK 5, KSB, SAN RAFAEL, ZARAGO... | 3 |  |  | 0.33732
2020-07-09 10:45 | JO12-0720-0099 | NEW CONNECTION/ PLUG CONNECTION |  | -(C)/ PUROK 5, KSB, SAN RAFAEL, ZARAGO... | 3 |  |  | 0.33732
2020-07-09 16:15 | JO12-0720-0107 | NEW CONNECTION/ PLUG CONNECTION |  | PRK 6, WEST, PFP, DEL PILAR, ZARAGOZA,... | 3 |  |  | 0.31323
2020-07-09 16:50 | JO12-0720-0108 | NEW CONNECTION/ PLUG CONNECTION |  | WEST, MADRE PALLA, DEL PILAR, ZARAGOZA... | 3 |  |  | 0.31323
2020-07-09 15:35 | JO12-0720-0114 | NEW CONNECTION/ TAPPING |  | PHASE 2, PUROK 2, RLC, CARMEN, ZARAGOZA, NUEVA... | 3 |  | 0.38553
2020-07-11 09:20 | JO12-0720-0056 | NEW CONNECTION/ TAPPING |  | PHASE 2, PUROK 1, EAP, CARMEN, ZARAGOZA, NUEVA... | 3 |  | 0.38553
2020-07-11 10:20 | JO12-0720-0119 | NEW CONNECTION/ TAPPING |  | PUROK 2, ROT, BATITANG, ZARAGOZA, NUEV... | 3 |  | 0.60237
2020-07-11 11:50 | JO12-0720-0168 | METERING CONCERNS (BUSTED PIPE) | 0.5 | DEL PILAR WEST, DEL PILAR, ZARAGOZA, N... | 70 | [11 empty] | 7.3087
2020-07-13 10:32 | JO12-0720-0102 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 1, MPM, STO. ROSARIO OLD, ZARAGO... | 3 |  |  | 0.38553
2020-07-13 09:56 | JO12-0720-0106 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 4,MAH, STO. ROSARIO YOUNG, ZARAG... | 3 |  |  | 0.36141
2020-07-13 15:26 | JO12-0720-0136 | METERING CONCERNS (BROKEN TAIL PIECE) | 0.5 | CONCEPCION (W), CONCEPCION, ZARAGOZA,... | 4 | [12 empty] | 0.51404
2020-07-13 14:40 | JO12-0720-0142 | METERING CONCERNS (BUSTED METER STAND) | 0.75 | DEL PILAR WEST, DEL PILAR, ZARAGOZA, N... | 66 | [11 empty] | 9.44
2020-07-13 16:18 | JO12-0720-0159 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 3, JCB, BATITANG, ZARAGOZA, NUEV... | 3 |  |  | 0.60237
2020-07-14 10:54 | JO12-0620-0191 | NEW CONNECTION/ TAPPING |  | PUROK LAKATAN, CONCEPCION WEST, ZARAGOZA, N... | 3 |  | 0.38553
2020-07-14 14:40 | JO12-0720-0071 | NEW CONNECTION/ TAPPING |  | PUROK 1, RMS, BATITANG, ZARAGOZA, NUEV... | 3 |  | 0.60237
2020-07-14 15:50 | JO12-0720-0113 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, AFA, MANAUL, ZARAGOZA, NUEVA... | 3 |  |  | 0.60237
2020-07-15 11:15 | JO12-0720-0127 | NEW CONNECTION/ TAPPING |  | PUROK 3, LDJ, MANAUL, ZARAGOZA, NUEVA... | 3 |  | 0.60237
2020-07-15 15:05 | JO12-0620-0219 | NEW CONNECTION/ TAPPING |  | PHASE 2, PUROK 5, RTD, SAN ISIDRO, ZARAGOZA, NU... | 3 |  | 0.43371
2020-07-15 10:30 | JO12-0720-0125 | NEW CONNECTION/ TAPPING |  | PUROK 6, EAB, SAN RAFAEL, ZARAGOZA, NU... | 3 |  | 0.33732
2020-07-15 11:50 | JO12-0720-0126 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 5, VQS, STA. LUCIA YOUNG, ZARAGO... | 3 |  |  | 0.19275
2020-07-15 15:30 | JO12-0720-0080 | NEW CONNECTION/ TAPPING |  | PUROK 2, RAR, BATITANG, ZARAGOZA, NUEV... | 3 |  | 0.60237
2020-07-15 13:35 | JO12-0720-0133 | NEW CONNECTION/ PLUG CONNECTION |  | PHASE 2, PUROK 2, JPI, SAN ISIDRO, ZARAGOZA, NU... | 3 |  |  | 0.43371
2020-07-16 14:35 | JO12-0520-0167 | SERVICE LEVEL (QUALITY OF WATER) | 0.75 | , PANTOC, ZARAGOZA, NUEVA ECIJA | 20 | [6 empty] | 4.4008
2020-07-16 10:55 | JO12-0720-0158 | REPAIRS AND MAINTENANCE (BUSTED PIPE) | 0.75 | PUROK 3, MACARSE, ZARAGOZA, NUEVA ECIJ... | 40 | [9 empty] | 4.89
2020-07-17 16:25 | JO12-0720-0172 | NEW CONNECTION/ PLUG CONNECTION |  | PHASE 2,LOT 13, BLOCK 3, AUC, CARMEN, ZARAGOZA... | 3 |  |  | 0.43371
2020-07-17 13:55 | JO12-0720-0175 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, MAC, GENERAL LUNA, ZARAGOZA,... | 3 |  |  | 0.60237
2020-07-18 15:45 | JO12-0720-0191 | REPAIRS AND MAINTENANCE (DRAIN FROM MAINLINE) | 2 | ZARAGOZA NATIONAL HIGH SCHOOL, SAN RAF... | 30 | [5 empty] | 9.1965
2020-07-20 11:40 | JO12-0720-0160 | NEW CONNECTION/ TAPPING |  | WEST, PDB, DEL PILAR, ZARAGOZA, NUEVA... | 3 |  | 0.31323
2020-07-20 13:55 | JO12-0720-0166 | NEW CONNECTION/ OPEN MAINLINE |  | PUROK 3, BPA, MAYAMOT, ZARAGOZA, NUEVA... | 3 |  |  | 0.19275
2020-07-20 15:07 | JO12-0720-0174 | NEW CONNECTION/ PLUG CONNECTION |  | EAST, PUROK BALINTAWAK, DEL PILAR, ZAR... | 3 |  |  | 0.28914
2020-07-20 14:38 | JO12-0720-0176 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, MDB, STO. ROSARIO OLD, ZARAGO... | 3 |  |  | 0.38553
2020-07-20 11:48 | JO12-0720-0195 | METERING CONCERNS (BUSTED METER STAND) | 0.5 | , STA. LUCIA YOUNG, ZARAGOZA, NUEVA EC... | 3 | [11 empty] | 0.19275
2020-07-21 14:18 | JO12-0720-0173 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 4B, JRL, BATITANG, ZARAGOZA, NUE... | 3 |  |  | 0.60237
2020-07-21 09:10 | JO12-0720-0198 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, JSR, MANAUL, ZARAGOZA, NUEVA... | 3 |  |  | 0.60237
2020-07-22 02:00 | JO12-0720-0212 | METERING CONCERNS (BUSTED PIPE) | 1 | PUROK 2, AFA, MANAUL, ZARAGOZA, NUEVA... | 180 | [9 empty] | 49.5108
2020-07-22 15:00 | JO12-0720-0202 | NEW CONNECTION/ PLUG CONNECTION |  | PHASE 1, PUROK 3, JDA, SAN ISIDRO, ZARAGOZA, NU... | 3 |  |  | 0.43371
2020-07-22 16:25 | JO12-0720-0215 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, AVM, PANTOC, ZARAGOZA, NUEVA... | 3 |  |  | 0.48189
2020-07-22 14:00 | JO12-0720-0217 | METERING CONCERNS (LEAK REPAIR) | 0.75 | , STA. LUCIA YOUNG, ZARAGOZA, NUEVA EC... | 30 | [11 empty] | 2.6406
2020-07-23 09:40 | JO12-0720-0223 | METERING CONCERNS (BUSTED METER STAND) | 0.5 | PHASE 1, CARMEN, ZARAGOZA, NUEVA ECIJA | 15 | [11 empty] | 1.9277
2020-07-24 15:15 | JO12-0720-0211 | NEW CONNECTION/ TAPPING ACROSS SOIL |  | PUROK 3, DAR, BATITANG, ZARAGOZA, NUEV... | 3 |  | 0.60237
2020-07-24 11:30 | JO12-0720-0227 | NEW CONNECTION/ TAPPING |  | PUROK 4, MCD, BATITANG, ZARAGOZA, NUEV... | 3 |  | 0.60237
2020-07-24 16:35 | JO12-0720-0203 | NEW CONNECTION/ TAPPING |  | PUROK 2, GPC, BATITANG, ZARAGOZA, NUEV... | 3 |  | 0.60237
2020-07-25 10:02 | JO12-0720-0197 | NEW CONNECTION/ TAPPING |  | PHASE 2,PUROK 1, MDM, CARMEN, ZARAGOZA, NUEVA... | 3 |  | 0.38553
2020-07-25 10:40 | JO12-0720-0226 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, MTA, GENERAL LUNA, ZARAGOZA,... | 3 |  |  | 0.60237
2020-07-27 15:00 | JO12-0720-0177 | NEW CONNECTION/ TAPPING |  | (A)WEST, BENITEZ SUBD.,MDA, CONCEPCION... | 3 |  | 0.38553
2020-07-27 11:50 | JO12-0720-0200 | NEW CONNECTION/ PLUG CONNECTION |  | PUROK 2, JTT, STO. ROSARIO YOUNG, ZARAGOZA, NUEVA ECIJA | 3 |  | 0.36141
2020-07-27 11:00 | JO12-0720-0219 | NEW CONNECTION/ TAPPING |  | SITIO PUTOT, EAST,RID, CONCEPCION, ZAR... | 3 |  | 0.48189
2020-07-27 08:35 | JO12-0720-0241 | REPAIRS AND MAINTENANCE (BUSTED PIPE) | 0.75 | PUROK 2, STA. LUCIA YOUNG, ZARAGOZA, N... | 25 | [9 empty] | 2.445
2020-07-27 14:15 | JO12-0720-0242 | REPAIRS AND MAINTENANCE (BUSTED PIPE) | 0.75 | PHASE 1,PUROK 5, SAN ISIDRO, ZARAGOZA, NUEVA E... | 75 | [9 empty] | 16.503
2020-07-27 09:30 | JO12-0720-0243 | REPAIRS AND MAINTENANCE (BUSTED PIPE) | 0.75 | PUROK 4, SAN RAFAEL, ZARAGOZA, NUEVA E... | 30 | [9 empty] | 5.1345
2020-07-28 17:31 | JO12-0820-0047 | METERING CONCERNS (BUSTED PIPE) | 0.75 | SITIO PUTOT,, BATITANG, ZARAGOZA, NUEV... | 13 | [9 empty] | 3.5758
TOTAL | [6 empty] | 9.2284 | 12.3847 | 0 | 0 | 9.1965 | 4.4008 | 0 | 0 | 256.4707 | 0 | 41.424 | 4.8511 | 0

## MPPR#5
BWSI - ZARAGOZA BRANCH
SAN ISIDRO, ZARAGOZA, NUEVA ECIJA
MONTHLY PUMP PRODUCTION REPORT
DATE: | June 30 to July29 |  |  | 29 | DAYS
PUMP STATION NO: |  | 5 ( BATITANG) |  |  |  | drain before flow meter
DATE | AVE | FLOWMETER READING |  | PROD | ADD: DRAIN | GROSPROD | GROS TTL | DRAIN | NET TTL | DISCHARGE/FLOWRATE |  |  | POWER INTERRUPTION
| PSI | START | ENDS | in cu.m | in cu.m | in cu.m | in hour | in hour | in hour | in cu.m/hr | in gal/min |  | TIME |  | NO. OF | PRODUCTION | AMOUNT OF | Cost of Diesel | REMARKS
[13 empty] | FROM | TO | HOURS | CU. M. | DIESEL | Per CU.M.
2020-06-30 | 55.4 | 174175 | 174266 | 91 | 2.9355 | 93.9355 | 2.5833 | 0.083333 | 2.5 | 35.2258 | 155.0934 | [6 empty] | #DIV/0!
2020-07-01 | 54 | 174266 | 174694 | 428 | 2.209 | 430.209 | 15.5 | 0.08 | 15.42 | 27.6129 | 121.575 | 1 | [5 empty] | #DIV/0!
2020-07-02 | 64 | 174694 | 175130 | 436 | 2.2503 | 438.2503 | 15.5 | 0.08 | 15.42 | 28.129 | 123.8474 | 2 | [5 empty] | #DIV/0!
2020-07-03 | 60.2 | 175130 | 175620 | 490 | 2.677 | 492.677 | 15.2533 | 0.083333 | 15.17 | 32.1241 | 141.4372 | 3 | [5 empty] | #DIV/0!
2020-07-04 | 47.16 | 175620 | 176141 | 521 | 2.8482 | 523.8482 | 15.2433 | 0.083333 | 15.16 | 34.1789 | 150.4839 | 4 | [5 empty] | #DIV/0!
2020-07-05 | 57.16 | 176141 | 176585 | 444 | 2.343 | 446.343 | 15.16 | 0.08 | 15.08 | 29.2876 | 128.9484 | 5 | [5 empty] | #DIV/0!
2020-07-06 | 52.57 | 176585 | 176994 | 409 | 2.236 | 411.236 | 15.2433 | 0.083333 | 15.16 | 26.8314 | 118.1342 | 6 | [5 empty] | #DIV/0!
2020-07-07 | 46.77 | 176994 | 177469 | 475 | 2.6105 | 477.6105 | 15.1633 | 0.083333 | 15.08 | 31.3256 | 137.9212 | 7 | [5 empty] | #DIV/0!
2020-07-08 | 49.33 | 177469 | 177946 | 477 | 2.5039 | 479.5039 | 15.24 | 0.08 | 15.16 | 31.2992 | 137.8052 | 8 | [5 empty] | #DIV/0!
2020-07-09 | 56.75 | 177946 | 178399 | 453 | 2.378 | 455.378 | 15.24 | 0.08 | 15.16 | 29.7244 | 130.8716 | 9 | [5 empty] | #DIV/0!
2020-07-10 | 56.75 | 178399 | 178799 | 400 | 2.0997 | 402.0997 | 15.24 | 0.08 | 15.16 | 26.2467 | 115.5599 | 10 | [5 empty] | #DIV/0!
2020-07-11 | 54.6 | 178799 | 179205 | 406 | 2.0955 | 408.0955 | 15.5 | 0.08 | 15.42 | 26.1935 | 115.3258 | 11 | [5 empty] | #DIV/0!
2020-07-12 | 51.33 | 179205 | 179613 | 408 | 2.1891 | 410.1891 | 14.91 | 0.08 | 14.83 | 27.3642 | 120.4799 | 12 | [5 empty] | #DIV/0!
2020-07-13 | 55.42 | 179613 | 180015 | 402 | 2.0978 | 404.0978 | 15.33 | 0.08 | 15.25 | 26.2231 | 115.4559 | 13 | [5 empty] | #DIV/0!
2020-07-14 | 65 | 180015 | 180429 | 414 | 2.1605 | 416.1605 | 15.33 | 0.08 | 15.25 | 27.0059 | 118.9023 | 14 | [5 empty] | #DIV/0!
2020-07-15 | 54.16 | 180429 | 180873 | 444 | 2.2931 | 446.2931 | 15.49 | 0.08 | 15.41 | 28.6637 | 126.2013 | 15 | [5 empty] | #DIV/0!
2020-07-16 | 57 | 180873 | 181329 | 456 | 2.3796 | 458.3796 | 15.33 | 0.08 | 15.25 | 29.7456 | 130.9649 | 16 | [5 empty] | #DIV/0!
2020-07-17 | 55.2 | 181329 | 181839 | 510 | 2.6476 | 512.6476 | 15.41 | 0.08 | 15.33 | 33.0954 | 145.7135 | 17 | [5 empty] | #DIV/0!
2020-07-18 | 48.6 | 181839 | 182365 | 526 | 2.7307 | 528.7307 | 15.41 | 0.08 | 15.33 | 34.1337 | 150.2849 | 18 | [5 empty] | #DIV/0!
2020-07-19 | 52.33 | 182365 | 182823 | 458 | 2.3777 | 460.3777 | 15.41 | 0.08 | 15.33 | 29.721 | 130.8564 | 19 | [5 empty] | #DIV/0!
2020-07-20 | 50.34 | 182823 | 183269 | 446 | 2.3536 | 448.3536 | 15.16 | 0.08 | 15.08 | 29.4195 | 129.5293 | 20 | [5 empty] | #DIV/0!
2020-07-21 | 49 | 183269 | 183734 | 465 | 2.4266 | 467.4266 | 15.33 | 0.08 | 15.25 | 30.3327 | 133.5497 | 21 | [5 empty] | #DIV/0!
2020-07-22 | 52.18 | 183734 | 184180 | 446 | 2.3275 | 448.3275 | 15.33 | 0.08 | 15.25 | 29.0933 | 128.0929 | 22 | [5 empty] | #DIV/0!
2020-07-23 | 44.8 | 184180 | 184614 | 434 | 2.2767 | 436.2767 | 15.25 | 0.08 | 15.17 | 28.459 | 125.3003 | 23 | [5 empty] | #DIV/0!
2020-07-24 | 50.37 | 184614 | 185039 | 425 | 2.1935 | 427.1935 | 15.5 | 0.08 | 15.42 | 27.4194 | 120.7228 | 24 | [5 empty] | #DIV/0!
2020-07-25 | 53.2 | 185039 | 185479 | 440 | 2.2593 | 442.2593 | 15.58 | 0.08 | 15.5 | 28.2413 | 124.3419 | 25 | [5 empty] | #DIV/0!
2020-07-26 | 49.42 | 185479 | 185920 | 441 | 2.2761 | 443.2761 | 15.5 | 0.08 | 15.42 | 28.4516 | 125.2677 | 26 | [5 empty] | #DIV/0!
2020-07-27 | 51 | 185920 | 186368 | 448 | 2.3258 | 450.3258 | 15.41 | 0.08 | 15.33 | 29.072 | 127.9993 | 27 | [5 empty] | #DIV/0!
2020-07-28 | 53.85 | 186368 | 186815 | 447 | 2.3327 | 449.3327 | 15.33 | 0.08 | 15.25 | 29.1585 | 128.3801 | 28 | [5 empty] | #DIV/0!
2020-07-29 | 52.85 | 186815 | 187174 | 359 | 2.1957 | 361.1957 | 13.08 | 0.08 | 13 | 27.4465 | 120.8423 | 29 | [5 empty] | #DIV/0!
2020-06-29 |  |  |  | 0 | 0 | 0 | 0.08 | 0.08 |  | 0 | 0 | 30 | [5 empty] | #DIV/0!
2020-06-30 |  | 0 |  | 0 | 0 | 0 | 12 | 0.08 |  | 0 | 0 | 31 | [5 empty] | #DIV/0!
TOTAL | 1600.74 |  |  | 12999 | 71.0303 | 13070.0303 | 457.0367 | 2.5767 | 442.54 | 881.2255 | 3879.8889 |  | TOTAL |  | 0 | 0 | 0 | #DIV/0!
AVE. | 55.1979 |  |  | 448.2414 | 2.4493 | 450.6907 | 15.7599 | 0.088851 | 15.26 | 30.3871 | 133.7893
PUMP OPERATORS: |  |  |  | 12999 |  |  |  | PREPARED BY:
Arman Justo | 7am-7pm | [6 empty] | ronald h samson
John Michael Duenas |  | 7pm-7am | [5 empty] | Operations Supervisor
Formulas:
DATE: = [DATE:, row above]+1
Note on H41: Joy Cenizal: 5pm cut-off

## MPPR#4
BWSI - ZARAGOZA BRANCH
SAN ISIDRO, ZARAGOZA, NUEVA ECIJA
MONTHLY PUMP PRODUCTION REPORT
DATE: | June 30 to July29 |  |  | 29 | DAYS
PUMP STATION NO: |  | 4 ( SAN VICENTE) |  |  |  | drain before flow meter
DATE | AVE | FLOWMETER READING |  | PROD | ADD: DRAIN | GROSPROD | GROS TTL | DRAIN | NET TTL | DISCHARGE/FLOWRATE |  |  | POWER INTERRUPTION
| PSI | START | ENDS | in cu.m | in cu.m | in cu.m | in hour | in hour | in hour | in cu.m/hr | in gal/min |  | TIME |  | NO. OF | PRODUCTION | AMOUNT OF |  | Cost of Diesel | REMARKS
[13 empty] | FROM | TO | HOURS | CU. M. | DIESEL |  | Per CU.M.
2020-06-30 | 50.6 | 387854 | 388067 | 213 | 3.3543 | 216.3543 | 5.08 | 0.08 | 5 | 41.9291 | 184.607 | [7 empty] | #DIV/0!
2020-07-01 | 61 | 388067 | 389014 | 947 | 4.1718 | 951.1718 | 18.16 | 0.08 | 18.08 | 52.1476 | 229.5971 | 1 | [6 empty] | #DIV/0!
2020-07-02 | 50.5 | 389014 | 390001 | 987 | 4.3673 | 991.3673 | 18.08 | 0.08 | 18 | 54.5907 | 240.3538 | 2 | [6 empty] | #DIV/0!
2020-07-03 | 48 | 390001 | 390975 | 974 | 4.3097 | 978.3097 | 18.08 | 0.08 | 18 | 53.8717 | 237.188 | 3 | [6 empty] | #DIV/0!
2020-07-04 | 42.83 | 390975 | 391932 | 957 | 4.2159 | 961.2159 | 18.16 | 0.08 | 18.08 | 52.6982 | 232.0216 | 4 | [6 empty] | #DIV/0!
2020-07-05 | 45.33 | 391932 | 392878 | 946 | 4.1858 | 950.1858 | 18.08 | 0.08 | 18 | 52.323 | 230.3695 | 5 | [6 empty] | #DIV/0!
2020-07-06 | 41.57 | 392878 | 393863 | 985 | 4.3392 | 989.3392 | 18.16 | 0.08 | 18.08 | 54.2401 | 238.8101 | 6 | [6 empty] | #DIV/0!
2020-07-07 | 41.57 | 393863 | 394834 | 971 | 4.2588 | 975.2588 | 18.24 | 0.08 | 18.16 | 53.2346 | 234.3833 | 7 | [6 empty] | #DIV/0!
2020-07-08 | 38.42 | 394834 | 395793 | 959 | 4.2061 | 963.2061 | 18.24 | 0.08 | 18.16 | 52.5768 | 231.4867 | 8
2020-07-09 | 45.33 | 395793 | 396747 | 954 | 4.2212 | 958.2212 | 18.08 | 0.08 | 18 | 52.7655 | 232.3176 | 9 | [6 empty] | #DIV/0!
2020-07-10 | 45.33 | 396747 | 397695 | 948 | 4.3914 | 952.3914 | 17.27 | 0.08 | 17.19 | 54.8929 | 241.6842 | 10 | 4:20pm | 5:07pm | 0.78333 | 34 | 146.88 | 0.1 | 4.32
2020-07-11 | 40 | 397695 | 398643 | 948 | 4.1579 | 952.1579 | 18.24 | 0.08 | 18.16 | 51.9737 | 228.8315 | 11 | [5 empty] | 0.083333 | #DIV/0!
2020-07-12 | 47.33 | 398643 | 399607 | 964 | 4.2467 | 968.2467 | 18.16 | 0.08 | 18.08 | 53.0837 | 233.7187 | 12 | [5 empty] | 0.25 | #DIV/0!
2020-07-13 | 52 | 399607 | 400502 | 895 | 3.9427 | 898.9427 | 18.16 | 0.08 | 18.08 | 49.2841 | 216.9899 | 13 | [6 empty] | #DIV/0!
2020-07-14 | 64.33 | 400502 | 401460 | 958 | 4.2389 | 962.2389 | 18.08 | 0.08 | 18 | 52.9867 | 233.2917 | 14 | [5 empty] | 0.13333 | #DIV/0!
2020-07-15 | 45.25 | 401460 | 402435 | 975 | 4.2952 | 979.2952 | 18.16 | 0.08 | 18.08 | 53.6894 | 236.3856 | 15 | [5 empty] | 0.21667 | #DIV/0!
2020-07-16 | 43.6 | 402435 | 403399 | 964 | 4.2655 | 968.2655 | 18.08 | 0.08 | 18 | 53.3186 | 234.7528 | 16 | [5 empty] | 0.18333 | #DIV/0!
2020-07-17 | 51.08 | 403399 | 404383 | 984 | 4.3158 | 988.3158 | 18.24 | 0.08 | 18.16 | 53.9474 | 237.5213 | 17 | [5 empty] | 0.13333 | #DIV/0!
2020-07-18 | 42.2 | 404383 | 405401 | 1018 | 4.4846 | 1022.4846 | 18.16 | 0.08 | 18.08 | 56.0573 | 246.8108 | 18 | [5 empty] | 0.48333 | #DIV/0!
2020-07-19 | 43 | 405401 | 406374 | 973 | 4.2675 | 977.2675 | 18.24 | 0.08 | 18.16 | 53.3443 | 234.8661 | 19 | [5 empty] | 0.16667 | #DIV/0!
2020-07-20 | 38.87 | 406374 | 407340 | 966 | 4.2555 | 970.2555 | 18.16 | 0.08 | 18.08 | 53.1938 | 234.2036 | 20 | [5 empty] | 0.15 | #DIV/0!
2020-07-21 | 40.25 | 407340 | 408304 | 964 | 4.2467 | 968.2467 | 18.16 | 0.08 | 18.08 | 53.0837 | 233.7187 | 21 | [5 empty] | 0.1 | #DIV/0!
2020-07-22 | 49.37 | 408304 | 409230 | 926 | 4.0793 | 930.0793 | 18.16 | 0.08 | 18.08 | 50.9912 | 224.5057 | 22 | [5 empty] | 0.25 | #DIV/0!
2020-07-23 | 38.71 | 409230 | 410188 | 958 | 4.4275 | 962.4275 | 17.31 | 0.08 | 17.23 | 55.3437 | 243.6692 | 23 | [5 empty] | 0.16667 | #DIV/0!
2020-07-24 | 38.63 | 410188 | 411161 | 973 | 4.2675 | 977.2675 | 18.24 | 0.08 | 18.16 | 53.3443 | 234.8661 | 24 | [5 empty] | 0.21667 | #DIV/0!
2020-07-25 | 45.12 | 411161 | 412115 | 954 | 4.6115 | 958.6115 | 16.55 | 0.08 | 16.47 | 57.6435 | 253.7947 | 25 | [5 empty] | 0.083333 | #DIV/0!
2020-07-26 | 32.73 | 412115 | 413089 | 974 | 4.2907 | 978.2907 | 18.16 | 0.08 | 18.08 | 53.6344 | 236.1432 | 26 | [5 empty] | 0.11667 | #DIV/0!
2020-07-27 | 37.85 | 413089 | 414059 | 970 | 4.2731 | 974.2731 | 18.16 | 0.08 | 18.08 | 53.4141 | 235.1734 | 27 | [5 empty] | 0.05 | #DIV/0!
2020-07-28 | 40.83 | 414059 | 415016 | 957 | 4.2345 | 961.2345 | 18.08 | 0.08 | 18 | 52.9314 | 233.0482 | 28 | [5 empty] | 0.05 | #DIV/0!
2020-07-29 | 39.68 | 415016 | 415757 | 741 | 4.5321 | 745.5321 | 13.08 | 0.08 | 13 | 56.6514 | 249.4266 | 29 | [5 empty] | 0.05 | #DIV/0!
TOTAL | 1341.31 |  |  | 27903 | 127.455 | 28030.455 | 523.21 | 2.4 | 520.81 | 1593.1869 | 7014.5364 |  | TOTAL |  | 0.78333 | 34 | 146.88 |  | 4.32
AVE. | 46.2521 |  |  | 962.1724 | 4.395 | 966.5674 | 18.0417 | 0.082759 | 17.959 | 54.9375 | 241.8806
PUMP OPERATORS: |  |  |  | #REF! |  |  |  | PREPARED BY:
Arman Justo | 7am-7pm | [6 empty] | ronald h samson
John Michael Duenas |  | 7pm-7am | [5 empty] | Operations Supervisor
Formulas:
DATE: = [DATE:, row above]+1

## MPPR#3
BWSI - ZARAGOZA BRANCH
SAN ISIDRO, ZARAGOZA, NUEVA ECIJA
MONTHLY PUMP PRODUCTION REPORT
DATE: | June 30 to July29 |  |  | 29 | DAYS
PUMP STATION NO: |  | 3 ( STO. ROSARIO ) |  |  |  | drain before flow meter
DATE | AVE | FLOWMETER READING |  | PROD | ADD: DRAIN | GROSPROD | GROS TTL | DRAIN | NET TTL | DISCHARGE/FLOWRATE |  |  | POWER INTERRUPTION
| PSI | START | ENDS | in cu.m | in cu.m | in cu.m | in hour | in hour | in hour | in cu.m/hr | in gal/min |  | TIME |  | NO. OF | PRODUCTION | AMOUNT OF | Cost of Diesel | REMARKS
[13 empty] | FROM | TO | HOURS | CU. M. | DIESEL | Per CU.M.
2020-06-30 | 50 | 652673 | 652912 | 239 | 5.3408 | 244.3408 | 3.58 | 0.08 | 3.5 | 66.7598 | 293.9322
2020-07-01 | 56 | 652912 | 653802 | 890 | 4.4279 | 894.4279 | 16.08 | 0.08 | 16 | 55.3483 | 243.6892 | 1
2020-07-02 | 55 | 653802 | 654692 | 890 | 4.4279 | 894.4279 | 16.08 | 0.08 | 16 | 55.3483 | 243.6892 | 2
2020-07-03 | 64 | 654692 | 655625 | 933 | 4.37 | 937.37 | 17.08 | 0.08 | 17 | 54.6253 | 240.5061 | 3
2020-07-04 | 52.5 | 655625 | 656569 | 944 | 4.4215 | 948.4215 | 17.08 | 0.08 | 17 | 55.2693 | 243.3416 | 4
2020-07-05 | 56.87 | 656569 | 657475 | 906 | 4.5075 | 910.5075 | 16.08 | 0.08 | 16 | 56.3433 | 248.0701 | 5
2020-07-06 | 51.75 | 657475 | 658354 | 879 | 4.3731 | 883.3731 | 16.08 | 0.08 | 16 | 54.6642 | 240.6773 | 6
2020-07-07 | 55.42 | 658354 | 659250 | 896 | 4.4577 | 900.4577 | 16.08 | 0.08 | 16 | 55.7214 | 245.332 | 7
2020-07-08 | 51.85 | 659250 | 660148 | 898 | 4.4677 | 902.4677 | 16.08 | 0.08 | 16 | 55.8458 | 245.8796 | 8
2020-07-09 | 50.71 | 660148 | 660999 | 851 | 4.2338 | 855.2338 | 16.08 | 0.08 | 16 | 52.9229 | 233.0106 | 9
2020-07-10 | 50.71 | 660999 | 661779 | 780 | 4.0336 | 784.0336 | 15.47 | 0.08 | 15.39 | 50.4202 | 221.9916 | 10 | 4:20pm | 5:30pm | 1.17 | 118 | 825 | 6.9915
2020-07-11 | 49.71 | 661779 | 662670 | 891 | 4.4328 | 895.4328 | 16.08 | 0.08 | 16 | 55.4104 | 243.963 | 11
2020-07-12 | 70.66 | 662670 | 663581 | 911 | 4.3957 | 915.3957 | 16.58 | 0.08 | 16.5 | 54.9457 | 241.9168 | 12
2020-07-13 | 64.75 | 663581 | 664395 | 814 | 4.0498 | 818.0498 | 16.08 | 0.08 | 16 | 50.6219 | 222.8797 | 13
2020-07-14 | 68.73 | 664395 | 665275 | 880 | 4.3781 | 884.3781 | 16.08 | 0.08 | 16 | 54.7264 | 240.9511 | 14
2020-07-15 | 60.42 | 665275 | 666092 | 817 | 4.0647 | 821.0647 | 16.08 | 0.08 | 16 | 50.8085 | 223.7012 | 15
2020-07-16 | 56 | 666092 | 667150 | 1058 | 5.2637 | 1063.2637 | 16.08 | 0.08 | 16 | 65.796 | 289.6889 | 16
2020-07-17 | 63.33 | 667150 | 668047 | 897 | 4.3281 | 901.3281 | 16.58 | 0.08 | 16.5 | 54.1013 | 238.1991 | 17
2020-07-18 | 55.5 | 668047 | 668939 | 892 | 4.4378 | 896.4378 | 16.08 | 0.08 | 16 | 55.4726 | 244.2368 | 18
2020-07-19 | 54.5 | 668939 | 669804 | 865 | 4.3035 | 869.3035 | 16.08 | 0.08 | 16 | 53.7935 | 236.844 | 19
2020-07-20 | 54.4 | 669804 | 670679 | 875 | 4.3532 | 879.3532 | 16.08 | 0.08 | 16 | 54.4154 | 239.582 | 20
2020-07-21 | 54.22 | 670679 | 671551 | 872 | 4.626 | 876.626 | 15.08 | 0.08 | 15 | 57.8249 | 254.5935 | 21
2020-07-22 | 56.87 | 671551 | 672399 | 848 | 4.2189 | 852.2189 | 16.08 | 0.08 | 16 | 52.7363 | 232.1892 | 22
2020-07-23 | 56.28 | 672399 | 673254 | 855 | 4.2537 | 859.2537 | 16.08 | 0.08 | 16 | 53.1716 | 234.1059 | 23
2020-07-24 | 57.43 | 673254 | 674118 | 864 | 4.2985 | 868.2985 | 16.08 | 0.08 | 16 | 53.7313 | 236.5701 | 24
2020-07-25 | 51.63 | 674118 | 674995 | 877 | 4.5032 | 881.5032 | 15.58 | 0.08 | 15.5 | 56.2901 | 247.836 | 25 | 5:20pm | 6:24pm | 1.07 | 81 | 450 | 5.5556
2020-07-26 | 56.62 | 674995 | 675866 | 871 | 4.3333 | 875.3333 | 16.08 | 0.08 | 16 | 54.1667 | 238.4868 | 26
2020-07-27 | 58 | 675866 | 676777 | 911 | 4.267 | 915.267 | 17.08 | 0.08 | 17 | 53.3372 | 234.835 | 27
2020-07-28 | 58.28 | 676777 | 677596 | 819 | 4.0746 | 823.0746 | 16.08 | 0.08 | 16 | 50.9328 | 224.2488 | 28
2020-07-29 | 59.75 | 677596 | 678318 | 722 | 4.7815 | 726.7815 | 12.08 | 0.08 | 12 | 59.7682 | 263.1495 | 29
TOTAL | 1701.89 |  |  | 25645 | 132.4256 | 25777.4256 | 467.79 | 2.4 | 465.39 | 1655.3197 | 7288.0968 |  | TOTAL |  | 2.24 | 199 | 1275 | 6.407
AVE. | 58.6859 |  |  | 884.3103 | 4.5664 | 888.8767 | 16.1307 | 0.082759 | 16.0479 | 57.08 | 251.3137
PUMP OPERATORS: |  |  |  | #REF! |  |  |  | PREPARED BY:
Arman Justo | 7am-7pm | [6 empty] | ronald h samson
John Michael Duenas |  | 7pm-7am | [5 empty] | Operations Supervisor
Formulas:
DATE: = [DATE:, row above]+1

## MPPR#2
BWSI - ZARAGOZA BRANCH
SAN ISIDRO, ZARAGOZA, NUEVA ECIJA
MONTHLY PUMP PRODUCTION REPORT
DATE: | June 30 to July29 |  |  | 29 | DAYS
PUMP STATION NO: |  | 2 ( STA. CRUZ ) |  |  |  | drain before flow meter
DATE | AVE | FLOWMETER READING |  | PROD | ADD: DRAIN | GROSPROD | GROS TTL | DRAIN | NET TTL | DISCHARGE/FLOWRATE |  |  | POWER INTERRUPTION
| PSI | START | ENDS | in cu.m | in cu.m | in cu.m | in hour | in hour | in hour | in cu.m/hr | in gal/min |  | TIME |  | NO. OF | PRODUCTION | AMOUNT OF | Cost of Diesel | REMARKS
[13 empty] | FROM | TO | HOURS | CU. M. | DIESEL | Per CU.M.
2020-06-30 | 61.6 | 158177 | 158337 | 160 | 2.9091 | 162.9091 | 4.5833 | 0.083333 | 4.5 | 34.9091 | 153.6989 | [5 empty] | 0 | #DIV/0!
2020-07-01 | 76.33 | 158337 | 159048 | 711 | 3.146 | 714.146 | 18.08 | 0.08 | 18 | 39.3252 | 173.1424 | 1 | [5 empty] | #DIV/0!
2020-07-02 | 63.5 | 159048 | 159791 | 743 | 3.424 | 746.424 | 18.0833 | 0.083333 | 18 | 41.0876 | 180.9017 | 2 | [5 empty] | #DIV/0!
2020-07-03 | 63.33 | 159791 | 160540 | 749 | 3.4516 | 752.4516 | 18.0833 | 0.083333 | 18 | 41.4194 | 182.3625 | 3 | [5 empty] | #DIV/0!
2020-07-04 | 50 | 160540 | 161308 | 768 | 3.5392 | 771.5392 | 18.0833 | 0.083333 | 18 | 42.47 | 186.9885 | 4 | [5 empty] | #DIV/0!
2020-07-05 | 45.54 | 161308 | 162054 | 746 | 3.4226 | 749.4226 | 18.1633 | 0.083333 | 18.08 | 41.0718 | 180.8321 | 5 | [5 empty] | #DIV/0!
2020-07-06 | 52.28 | 162054 | 162776 | 722 | 3.3272 | 725.3272 | 18.0833 | 0.083333 | 18 | 39.9263 | 175.7887 | 6 | [5 empty] | #DIV/0!
2020-07-07 | 56 | 162776 | 163511 | 735 | 3.3871 | 738.3871 | 18.0833 | 0.083333 | 18 | 40.6452 | 178.9539 | 7 | [5 empty] | #DIV/0!
2020-07-08 | 51.85 | 163511 | 164257 | 746 | 3.4378 | 749.4378 | 18.0833 | 0.083333 | 18 | 41.2535 | 181.6321 | 8 | [5 empty] | #DIV/0!
2020-07-09 | 61.37 | 164257 | 164965 | 708 | 3.2627 | 711.2627 | 18.0833 | 0.083333 | 18 | 39.1521 | 172.3801 | 9 | [5 empty] | #DIV/0!
2020-07-10 | 50.1 | 164965 | 165698 | 733 | 3.2434 | 736.2434 | 18.08 | 0.08 | 18 | 40.542 | 178.4998 | 10 | 16:53 | 18:38 | 1.75 | 73 | 453.13 | 6.2073
2020-07-11 | 60.16 | 165698 | 166432 | 734 | 3.3825 | 737.3825 | 18.0833 | 0.083333 | 18 | 40.5899 | 178.7104 | 11 | [5 empty] | #DIV/0!
2020-07-12 | 58.83 | 166432 | 167135 | 703 | 3.2396 | 706.2396 | 18.0833 | 0.083333 | 18 | 38.8756 | 171.1627 | 12 | [5 empty] | #DIV/0!
2020-07-13 | 59.66 | 167135 | 167816 | 681 | 3.0133 | 684.0133 | 18.08 | 0.08 | 18 | 37.6659 | 165.8368 | 13 | [5 empty] | #DIV/0!
2020-07-14 | 76 | 167816 | 168541 | 725 | 3.3263 | 728.3263 | 18.1633 | 0.083333 | 18.08 | 39.9156 | 175.7416 | 14 | [5 empty] | #DIV/0!
2020-07-15 | 63.66 | 168541 | 169259 | 718 | 3.3088 | 721.3088 | 18.0833 | 0.083333 | 18 | 39.7051 | 174.8148 | 15 | [5 empty] | #DIV/0!
2020-07-16 | 64.8 | 169259 | 169967 | 708 | 3.2483 | 711.2483 | 18.1633 | 0.083333 | 18.08 | 38.9796 | 171.6208 | 16 | [5 empty] | #DIV/0!
2020-07-17 | 59.6 | 169967 | 170715 | 748 | 3.2952 | 751.2952 | 18.16 | 0.08 | 18.08 | 41.1894 | 181.3502 | 17 | [5 empty] | #DIV/0!
2020-07-18 | 56.8 | 170715 | 171466 | 751 | 3.4608 | 754.4608 | 18.0833 | 0.083333 | 18 | 41.53 | 182.8495 | 18 | [5 empty] | #DIV/0!
2020-07-19 | 56.28 | 171466 | 172207 | 741 | 3.3997 | 744.3997 | 18.1633 | 0.083333 | 18.08 | 40.7965 | 179.6201 | 19 | [5 empty] | #DIV/0!
2020-07-20 | 56 | 172207 | 172936 | 729 | 3.2115 | 732.2115 | 18.16 | 0.08 | 18.08 | 40.1432 | 176.7437 | 20 | [5 empty] | #DIV/0!
2020-07-21 | 53.37 | 172936 | 173673 | 737 | 3.3963 | 740.3963 | 18.0833 | 0.083333 | 18 | 40.7558 | 179.4408 | 21 | [5 empty] | #DIV/0!
2020-07-22 | 58 | 173673 | 174382 | 709 | 3.2673 | 712.2673 | 18.0833 | 0.083333 | 18 | 39.2074 | 172.6235 | 22 | [5 empty] | #DIV/0!
2020-07-23 | 50.85 | 174382 | 175105 | 723 | 3.3318 | 726.3318 | 18.0833 | 0.083333 | 18 | 39.9816 | 176.0322 | 23 | [5 empty] | #DIV/0!
2020-07-24 | 56.25 | 175105 | 175855 | 750 | 3.441 | 753.441 | 18.1633 | 0.083333 | 18.08 | 41.292 | 181.8017 | 24 | [5 empty] | #DIV/0!
2020-07-25 | 60.85 | 175855 | 176590 | 735 | 7.7597 | 742.7597 | 7.8933 | 0.083333 | 7.81 | 93.1166 | 409.9767 | 25 | 17:20 | 17:50 | 0.5 | 24 | 93.75 | 3.9062
2020-07-26 | 56.42 | 176590 | 177322 | 732 | 3.3584 | 735.3584 | 18.1633 | 0.083333 | 18.08 | 40.301 | 177.4385 | 26 | [5 empty] | #DIV/0!
2020-07-27 | 57.57 | 177322 | 178036 | 714 | 3.2758 | 717.2758 | 18.1633 | 0.083333 | 18.08 | 39.31 | 173.0752 | 27 | [5 empty] | #DIV/0!
2020-07-28 | 56.57 | 178036 | 178755 | 719 | 3.2988 | 722.2988 | 18.1633 | 0.083333 | 18.08 | 39.5852 | 174.2872 | 28 | [5 empty] | #DIV/0!
2020-07-29 | 55.11 | 178755 | 179287 | 532 | 3.2638 | 535.2638 | 13.5833 | 0.083333 | 13.5 | 39.1656 | 172.4398 | 29 | [5 empty] | #DIV/0!
TOTAL | 1748.68 |  |  | 21110 | 103.8294 | 21213.8294 | 515.0933 | 2.4833 | 512.61 | 1253.9078 | 5520.7469 |  | TOTAL |  | 2.25 | 97 | 546.88 | 5.6379
AVE. | 60.2993 |  |  | 727.931 | 3.5803 | 731.5114 | 17.7618 | 0.085632 | 17.6762 | 43.2382 | 190.3706
PUMP OPERATORS: |  |  |  | #REF! |  |  |  | PREPARED BY:
Arman Justo | 7am-7pm | [6 empty] | ronald samson
John Michael Duenas |  | 7pm-7am | [5 empty] | Operations Supervisor
Formulas:
DATE: = [DATE:, row above]+1

## MPPR#1
BWSI - ZARAGOZA BRANCH
SAN ISIDRO, ZARAGOZA, NUEVA ECIJA
MONTHLY PUMP PRODUCTION REPORT
DATE: | June 30 to July 29 |  |  | 29 | DAYS
PUMP STATION NO: |  | 1 ( SAN ISIDRO ) |  |  |  | drain before flow meter
DATE | AVE | FLOWMETER READING |  | PROD | ADD: DRAIN | GROSPROD | GROS TTL | DRAIN | NET TTL | DISCHARGE/FLOWRATE |  |  | POWER INTERRUPTION | [5 empty] | REMARKS
| PSI | START | ENDS | in cu.m | in cu.m | in cu.m | in hour | in hour | in hour | in cu.m/hr | in gal/min |  | TIME |  | NO. OF | PRODUCTION | AMOUNT OF | Cost of Diesel
[13 empty] | FROM | TO | HOURS | CU. M. | DIESEL | Per CU.M.
2020-06-30 | 59.5 | 216924 | 217462 | 538 | 0 | 538 | 7 | 0 | 7 | 76.8571 | 338.3892 | [6 empty] | #DIV/0!
2020-07-01 | 50.76 | 217462 | 219270 | 1808 | 0 | 1808 | 24 | 0 | 24 | 75.3333 | 331.6801 | 1 | [5 empty] | #DIV/0!
2020-07-02 | 54.37 | 219270 | 221102 | 1832 | 0 | 1832 | 24 | 0 | 24 | 76.3333 | 336.0829 | 2 | [5 empty] | #DIV/0!
2020-07-03 | 57.17 | 221102 | 222813 | 1711 | 0 | 1711 | 24 | 0 | 24 | 71.2917 | 313.8853 | 3 | [5 empty] | #DIV/0!
2020-07-04 | 52.82 | 222813 | 224416 | 1603 | 0 | 1603 | 24 | 0 | 24 | 66.7917 | 294.0726 | 4 | [5 empty] | #DIV/0!
2020-07-05 | 54.94 | 224416 | 226269 | 1853 | 0 | 1853 | 24 | 0 | 24 | 77.2083 | 339.9354 | 5 | [5 empty] | #DIV/0!
2020-07-06 | 54.1 | 226269 | 227990 | 1721 | 0 | 1721 | 24 | 0 | 24 | 71.7083 | 315.7198 | 6 | [5 empty] | #DIV/0!
2020-07-07 | 55.38 | 227990 | 229763 | 1773 | 0 | 1773 | 24 | 0 | 24 | 73.875 | 325.2593 | 7 | [5 empty] | #DIV/0!
2020-07-08 | 52.23 | 229763 | 231523 | 1760 | 0 | 1760 | 24 | 0 | 24 | 73.3333 | 322.8744 | 8 | [5 empty] | #DIV/0!
2020-07-09 | 55.17 | 231523 | 233373 | 1850 | 0 | 1850 | 24 | 0 | 24 | 77.0833 | 339.3851 | 9 | [5 empty] | #DIV/0!
2020-07-10 | 53.72 | 233373 | 235238 | 1865 | 6.4283 | 1871.4283 | 23.21 | 0.08 | 23.13 | 80.3533 | 353.7822 | 10 | 16:45 | 18:31 | 1.77 | 149 | 456.25 | 3.0621
2020-07-11 | 53.72 | 235238 | 237090 | 1852 | 0 | 1852 | 24 | 0 | 24 | 77.1667 | 339.752 | 11 | [5 empty] | #DIV/0!
2020-07-12 | 52.95 | 237090 | 238873 | 1783 | 0 | 1783 | 24 | 0 | 24 | 74.2917 | 327.0938 | 12 | [5 empty] | #DIV/0!
2020-07-13 | 56.68 | 238873 | 240545 | 1672 | 0 | 1672 | 24 | 0 | 24 | 69.6667 | 306.7307 | 13 | [5 empty] | #DIV/0!
2020-07-14 | 62.36 | 240545 | 242367 | 1822 | 0 | 1822 | 24 | 0 | 24 | 75.9167 | 334.2484 | 14 | [5 empty] | #DIV/0!
2020-07-15 | 57.35 | 242367 | 244216 | 1849 | 0 | 1849 | 24 | 0 | 24 | 77.0417 | 339.2016 | 15 | [5 empty] | #DIV/0!
2020-07-16 | 58.42 | 244216 | 245969 | 1753 | 0 | 1753 | 24 | 0 | 24 | 73.0417 | 321.5903 | 16 | [5 empty] | #DIV/0!
2020-07-17 | 57 | 245969 | 247713 | 1744 | 0 | 1744 | 24 | 0 | 24 | 72.6667 | 319.9392 | 17 | [5 empty] | #DIV/0!
2020-07-18 | 54.05 | 247713 | 249538 | 1825 | 0 | 1825 | 24 | 0 | 24 | 76.0417 | 334.7988 | 18 | [5 empty] | #DIV/0!
2020-07-19 | 50.89 | 249538 | 251352 | 1814 | 0 | 1814 | 24 | 0 | 24 | 75.5833 | 332.7808 | 19 | [5 empty] | #DIV/0!
2020-07-20 | 53.31 | 251352 | 253116 | 1764 | 0 | 1764 | 24 | 0 | 24 | 73.5 | 323.6083 | 20 | [5 empty] | #DIV/0!
2020-07-21 | 52 | 253116 | 254868 | 1752 | 0 | 1752 | 24 | 0 | 24 | 73 | 321.4068 | 21 | [5 empty] | #DIV/0!
2020-07-22 | 55.76 | 254868 | 256713 | 1845 | 0 | 1845 | 24 | 0 | 24 | 76.875 | 338.4678 | 22 | [5 empty] | #DIV/0!
2020-07-23 | 53.37 | 256713 | 258606 | 1893 | 0 | 1893 | 24 | 0 | 24 | 78.875 | 347.2735 | 23 | [5 empty] | #DIV/0!
2020-07-24 | 55 | 258606 | 260498 | 1892 | 0 | 1892 | 24 | 0 | 24 | 78.8333 | 347.09 | 24 | [5 empty] | #DIV/0!
2020-07-25 | 53.68 | 260498 | 262358 | 1860 | 0 | 1860 | 24 | 0 | 24 | 77.5 | 341.2196 | 25 | 17:00 | 17:35 | 5.8333 | 47 | 109.38 | 2.3272
2020-07-26 | 51.84 | 262358 | 264252 | 1894 | 0 | 1894 | 24 | 0 | 24 | 78.9167 | 347.4569 | 26 | [5 empty] | #DIV/0!
2020-07-27 | 50.9 | 264252 | 266061 | 1809 | 0 | 1809 | 24 | 0 | 24 | 75.375 | 331.8636 | 27 | [5 empty] | #DIV/0!
2020-07-28 | 59.1 | 266061 | 267895 | 1834 | 0 | 1834 | 24 | 0 | 24 | 76.4167 | 336.4498 | 28 | [5 empty] | #DIV/0!
2020-07-29 | 54.47 | 267895 | 269230 | 1335 | 0 | 1335 | 17 | 0 | 17 | 78.5294 | 345.7519 | 29 | [5 empty] | #DIV/0!
TOTAL | 1643.01 |  |  | 52306 | 6.4283 | 52312.4283 | 695.21 | 0.08 | 695.13 | 2259.4065 | 9947.7903 |  | TOTAL |  | 7.6033 | 196 | 565.63 | 2.8859
AVE. | 56.6555 |  |  | 1803.6552 | 0.22166 | 1803.8768 | 23.9728 | 0.0027586 | 23.97 | 77.9106 | 343.0273
PUMP OPERATORS: |  |  |  | 52306 |  |  |  | PREPARED BY:
Arman Justo | 7am-7pm | [6 empty] | ronald h samson
John Michael Duenas |  | 7pm-7am | [5 empty] | Operations Supervisor
Formulas:
DATE: = [DATE:, row above]+1

## W.B. Input Data
BWSI- ZARAGOZA BRANCH
As of July 2020
0
| Cubic | Remarks
Meter
I. Supply | 140404.1685
- Pump Production | 139963
- Pump Drain (add back) | 441.1685
- Purchased Bulk Water
II. Authorized Consumption
II.A. Billed Authorized Consumption
II.A.1. Billed Metered Consumption | 124005
- Customer's Consumption | 124005
- Residential | 119963
- Commercial | 4042
- Bulk Water | 0
II.A.2. Billed Unmetered Consumption | 0
- Bulk Water
- Lorry | 0
- Contractor's Usage
II.B. Unbilled Authorized Consumption
II.B.1. Unbilled Metered Consumption | 80
- Office Usage
- Pump Houses Usage | 80
- Discount to Customers
II.B.2. Unbilled Unmetered Consumption | 476.3789
- Service Connection Draining | 21.6131
- Tapping | 9.2284
- Across Pavement
- Plug Connection | 12.3847
- Relocate Meter
- Pump/Line Draining | 454.7658
- Line Draining - Mainline | 9.1965
- Line Draining - Meter Stand | 4.4008
- Pump Draining | 441.1685
- Backwash
- Fire Usage
III. Water Losses
III.A. Commercial/Apparent Losses
III.A.1. Unauthorized Consumption | 0
- Illegal Connection
III.A.2. Metering Inaccuracies | 0
- Meter Test (Under Registering or Under Read)
III.B. Real/Physical Losses
III.B.1 Accounted Leakage | 302.7458
- Busted Service Pipes | 256.4707
- Busted Mainlines | 0
- Busted Meter Stand | 41.424
- Tail Piece Leak | 4.8511
- Gate Valve Leak | 0
- Disconnect Mainline
- Disconnect Meter Stand
- Installation of Appurtenances | 0
- Interconnection of Mainline | 0
III.B.2 Unaccounted Leakage | 15540.0438
Note: Fill-up the Yellow Cell

## Water Balance
BWSI- ZARAGOZA BRANCH
As of July 2020
Billed Metered Consumption
|  | Billed Authorized | 124005 | Revenue
|  | Consumption | 88.32% | Water
|  | 124005 | Billed Unmetered Consumption | 124005
| Authorized | 88.32% | 0 | 88.32%
| Consumption |  | 0%
| 124561.3789 |  | Unbilled Metered Consumption
| 88.72% | Unbilled Authorized | 80
|  | Consumption | 0.05698%
|  | 556.3789 | Unbilled Unmetered Consumption
|  | 0.3963% | 476.3789
SUPPLY |  |  | 0.3393%
140404.1685 |  |  | Unauthorized Consumption
|  | Commercial / | 0 | Non-Revenue
|  | Apparent Losses | 0% | Water
|  | 0 | Metering Inaccuracies | 16399.1685
| Water | 0% | 0 | 11.68%
| Losses |  | 0%
| 15842.7896 |  | Accounted Leakage
| 11.28% | Real /Physical | 302.7458
|  | Losses | 0.2156%
|  | 15842.7896 | Unaccounted Leakage
|  | 11.28% | 15540.0438
11.07%

## Pump Lowest & Highest PSI
Pump Lowest & Highest PSI
| Pump 1 (San Isidro) |  | Pump 2 (Sta. Cruz) |  | Pump 3 (Sto. Rosario) |  | Pump 4 (San Vicente) |  | Pump 5 (Batitang)
Date | Lowest PSI | Highest PSI | Lowest PSI | Highest PSI | Lowest PSI | Highest PSI | Lowest PSI | Highest PSI | Lowest PSI | Highest PSI
2020-06-29 | 30 | 70 | 30 | 77 | 48 | 85 | 45 | 88 | 40 | 70
2020-06-30 | 35 | 70 | 30 | 78 | 40 | 80 | 45 | 82 | 45 | 70
2020-07-01 | 32 | 70 | 45 | 78 | 35 | 80 | 63 | 88 | 40 | 72
2020-07-02 | 60 | 70 | 25 | 73 | 35 | 80 | 35 | 86 | 32 | 70
2020-07-03 | 50 | 70 | 26 | 75 | 45 | 95 | 48 | 85 | 35 | 70
2020-07-04 | 30 | 70 | 20 | 80 | 30 | 100 | 32 | 85 | 28 | 72
2020-07-05 | 35 | 70 | 24 | 77 | 37 | 85 | 30 | 80 | 35 | 70
2020-07-06 | 32 | 70 | 18 | 80 | 30 | 85 | 35 | 85 | 30 | 72
2020-07-07 | 32 | 70 | 35 | 78 | 33 | 80 | 38 | 83 | 30 | 70
2020-07-08 | 33 | 70 | 18 | 75 | 33 | 90 | 35 | 80 | 30 | 72
2020-07-09 | 45 | 70 | 20 | 78 | 28 | 85 | 40 | 80 | 30 | 70
2020-07-10 | 36 | 70 | 20 | 78 | 28 | 85 | 50 | 80 | 30 | 70
2020-07-11 | 35 | 70 | 20 | 75 | 40 | 85 | 30 | 85 | 28 | 70
2020-07-12 | 30 | 70 | 18 | 75 | 38 | 95 | 30 | 85 | 30 | 72
2020-07-13 | 60 | 70 | 20 | 77 | 35 | 95 | 35 | 60 | 40 | 72
2020-07-14 | 30 | 70 | 50 | 80 | 45 | 90 | 65 | 85 | 40 | 72
2020-07-15 | 42 | 70 | 18 | 77 | 30 | 85 | 35 | 86 | 35 | 72
2020-07-16 | 40 | 70 | 20 | 82 | 36 | 85 | 42 | 90 | 35 | 72
2020-07-17 | 30 | 70 | 35 | 80 | 45 | 90 | 40 | 90 | 30 | 72
2020-07-18 | 35 | 70 | 17 | 78 | 33 | 85 | 32 | 90 | 29 | 72
2020-07-19 | 35 | 70 | 20 | 80 | 32 | 85 | 35 | 90 | 28 | 72
2020-07-20 | 35 | 70 | 18 | 75 | 30 | 95 | 35 | 88 | 30 | 72
2020-07-21 | 42 | 70 | 19 | 78 | 32 | 92 | 34 | 90 | 30 | 72
2020-07-22 | 24 | 70 | 25 | 80 | 40 | 85 | 40 | 85 | 40 | 70
2020-07-23 | 33 | 70 | 16 | 80 | 35 | 95 | 28 | 85 | 28 | 72
2020-07-24 | 30 | 70 | 22 | 78 | 37 | 100 | 37 | 88 | 32 | 70
2020-07-25 | 30 | 70 | 25 | 75 | 35 | 90 | 40 | 85 | 30 | 70
2020-07-26 | 33 | 70 | 15 | 78 | 35 | 85 | 30 | 85 | 28 | 70
2020-07-27 | 38 | 70 | 15 | 79 | 35 | 95 | 35 | 90 | 25 | 70
2020-07-28 | 35 | 70 | 20 | 77 | 33 | 90 | 30 | 90 | 40 | 70
2020-07-29 | 40 | 70 | 20 | 75 | 30 | 95 | 35 | 88
2020-07-30 | 40 | 70 | 30 | 80 | 48 | 95 | 42 | 88
2020-07-31 | 36 | 70 | 17 | 78 | 38 | 90 | 32 | 90
| 24 | 70 | 15 | 82 | 90 | 100 | 28 | 90 | 25 | 72
Pump 1 | 24 | 70
Pump 2 | 15 | 82
Pump 3 | 90 | 100
Pump 4 | 28 | 90
Pump 5 | 25 | 72
L/ H | 15 | 100
Ave. L/ Ave. H | 36.4 | 82.8
Formulas:
Date = [Date, row above]+1